## General Electrical Requirements

Effective:   July 1, 2025

This special provision replaces Articles 801.01 – 801.07, 801.09 – 801-16 of the Standard Specifications.

Definition.  Codes, standards, and industry specifications cited for electrical work shall be by definition the latest adopted version thereof, unless indicated otherwise.

Materials shall include electrical equipment, fittings, devices, motors, appliances, fixtures, apparatus, all hardware and appurtenances, and the like, used as part of, or in connection with, electrical installation.

Standards of Installation.  Materials shall be installed according to the manufacturer’s recommendations, the NEC, OSHA, the NESC, and AASHTO’s Standard Specifications for Structural Supports for Highway Signs, Luminaires, and Traffic Signals.

All like materials shall be from the same manufacturer.  Listed and labeled materials shall be used whenever possible.  The listing shall be according to UL or an approved equivalent.

Safety and Protection.  Safety and protection requirements shall be as follows.

Safety.  Electrical systems shall not be left in an exposed or otherwise hazardous condition.  All electrical boxes, cabinets, pole handholes, etc. which contain wiring, either energized or non-energized, shall be closed or shall have covers in place and be locked when possible, during nonworking hours.

Protection.  Electrical raceway or duct openings shall be capped or otherwise sealed from the entrance of water and dirt.  Wiring shall be protected from mechanical injury.

Equipment Grounding Conductor.  All electrical systems, materials, and appurtenances shall be grounded.  Good ground continuity throughout the electrical system shall be assured, even though every detail of the requirements is not specified or shown.  Electrical circuits shall have a continuous insulated equipment grounding conductor.  When metallic conduit is used, it shall be bonded to the equipment grounding conductor, but shall not be used as the equipment grounding conductor.

Detector loop lead-in circuits, circuits under 50 volts, and runs of fiber optic cable will not require an equipment grounding conductor.

Where connections are made to painted surfaces, the paint shall be scraped to fully expose metal at the connection point.  After the connection is completed, the paint system shall be repaired to the satisfaction of the Engineer.

Bonding of all boxes and other metallic enclosures throughout the wiring system to the equipment grounding conductor shall be made using a splice and pigtail connection.  Mechanical connectors shall have a serrated washer at the contact surface.

All connections to structural steel or fencing shall be made with exothermic welds.  Care shall be taken not to weaken load carrying members.  Where connections are made to epoxy coated reinforcing steel, the epoxy coating shall be sufficiently removed to facilitate a mechanical connection.  The epoxy coating shall be repaired to the satisfaction of the Engineer.  Where connections are made to insulated conductors, the connection shall be wrapped with at least four layers of electrical tape extended 6 in. (150 mm) onto the conductor insulation.

Submittals.  At the preconstruction meeting, the Contractor shall submit a written listing of manufacturers for all major electrical and mechanical items.  The list of manufacturers shall be binding, except by written request from the Contractor and approval by the Engineer.  The request shall include acceptable reasons and documentation for the change.

Within 30 calendar days after contract execution, the Contractor shall submit, for approval, through the method as directed in the pre-construction meeting. Submittals for the materials for each individual pay item shall be complete in every respect.  Submittals which include multiple pay items shall have all submittal material for each item or group of items covered by a particular specification, grouped together and the applicable pay item identified.  Various submittals shall, when taken together, form a complete coordinated package.  A partial submittal will be returned without review unless prior written permission is obtained from the Engineer.

Submittals shall be provided for all items used, temporary and permanent, for review and approval.

Equipment which will be owned and maintained by a local agency other than the State shall be reviewed and approved by that agency prior to submittal to the State. The submittal to the State shall include any comments made by the local agency.

Each PDF document must be a vector format PDF from the originating supplier or program and not scanned images.

The submittal must clearly identify the specific model number or catalog number of the item being proposed. Submittals must be the Manufacturers current published information. Out of date submittal material will be grounds for rejection.

Contractor: Contractor Name

Pay Item: X0327607

Route: I-00

Section: 2013-xxx-yzx

County: Cook

Contract: 12Z34

The submittal shall be properly identified by Contractor, Pay Item Number, route, section, county, and contract number. Example:

The Contractor shall have reviewed the submittal material and affixed the Contractor’s stamp of approval, with date and signature, for each individual item prior to submittal.  The Contractor’s approval stamp shall be the first page of the submittal.

Illegible print, incompleteness, inaccuracy, or lack of coordination will be grounds for rejection.

Items from multiple disciplines shall not be combined on a single submittal and transmittal.  Items for lighting, signals, surveillance, and CCTV must be in separate submittals since they may be reviewed by various personnel in various locations.

The Department may provide a list of pay items broken out by discipline upon request for a particular contract. In general, the disciplines are as follows:

| Discipline | Typical Items |
| --- | --- |
| ITS | CCTV CCTV structures Communication vaults Fiber optic Fiber optic duct Network equipment |
| Lighting | Breakaway devices Light poles Light tower Lighting cables Lighting controllers Luminaires Unit duct |
| Pump Station | All pump station equipment |
| Signing | Signing |
| Surveillance | Loop cables Detector equipment & associated structures Ramp metering & associated structures Wireless pavement sensors and assoc. structures Radar detection Data Probing Handholes Dynamic Message Signs (DMS) |
| Traffic Signal | Controllers/Cabinets Handholes Illuminated signs Pedestrian Push Buttons Signal Cable Signal Detectors Signal Heads Signal Loop Cable Signal Modules Signal Structures |
| Local Roads Lighting | Same as lighting |
| Local Roads Traffic Signal | Same as traffic signal |
| Discipline with the predominate amount of work in contract or ask Engineer. | Raceways Electric cables Junction boxes |

The Engineer will review the submittals for conformance with the design concept of the project according to Article 105.04 and the following.  The Engineer will stamp the drawings indicating their status as “Approved”, “Approved as Noted”, “Disapproved”, “Incomplete”, or “Information Only”.  Since the Engineer’s review is for conformance with the design concept only, it shall be the Contractor’s responsibility to coordinate the various items into a working system as specified.  The Contractor shall not be relieved from responsibility for errors or omissions in the shop, working, or layout drawings by the Engineer’s approval thereof.  The Contractor shall still be in full compliance with contract and specification requirements.

All submitted items reviewed and marked “Disapproved”, “Incomplete” or “Approved as Noted” shall be resubmitted by the Contractor in their entirety, unless otherwise indicated within the submittal comments.

Work shall not begin until the Engineer has approved the submittal.  Material installed prior to approval by the Engineer, will be subject to removal and replacement at no additional cost to the Department.

Certifications.  When certifications are specified and are available prior to material manufacture, the certification shall be included in the submittal information.  When specified and only available after manufacture, the submittal shall include a statement of intent to furnish certification.  All certificates shall be complete with all appropriate test dates and data.

Authorized Project Delay.  See Article 801.08

Maintenance transfer and Preconstruction Inspection:

General.  Before performing any excavation, removal, or installation work (electrical or otherwise) at the site, the Contractor shall request a maintenance transfer and preconstruction site inspection, to be held in the presence of the Engineer and a representative of the party or parties responsible for maintenance of any electrical systems (lighting, ITS, Pump Station, Surveillance, and traffic control systems) which may be affected by the work.  The request for the maintenance transfer and preconstruction inspection shall be made no less than fourteen (14) calendar days prior to the desired inspection date.  The maintenance transfer and preconstruction inspection shall:

Establish the procedures for formal transfer of maintenance responsibility required for the construction period.

Establish the approximate location and operating condition of the electrical systems which may be affected by the work.

Marking of Existing Cable Systems.  The party responsible for maintenance of any existing electrical systems at the project site will, at the Contractor's request, mark and/or stake, once per location, all underground cable routes owned or maintained by the State.  A project may involve multiple "locations" where separated electrical systems are involved (i.e. different controllers).  The markings shall be taken to have a horizontal tolerance of at least 1 foot (304.8 mm) to either side.  The request for the cable locations and marking shall be made at the same time the request for the maintenance transfer and preconstruction inspection is made.  The Contractor shall exercise extreme caution where existing buried cable runs are involved.  The markings of existing systems are made strictly for assistance to the Contractor and this does not relieve the Contractor of responsibility for the repair or replacement of any cable run damaged in the course of his work, as specified elsewhere herein.  Note that the contractor shall be entitled to only one request for location marking of existing systems and that multiple requests may only be honored at the contractor's expense.  No locates will be made after maintenance is transferred unless it is at the contractor’s expense.

Condition of Existing Systems.  The Contractor shall conduct an inventory of all existing electrical system equipment within the project limits, which may be affected by the work, making note of any parts which are found broken or missing, defective or malfunctioning.  Megger and load readings shall be taken for all existing circuits which will remain in place or be modified.  If a circuit is to be taken out in its entirety, then readings do not have to be taken.   The inventory and test data shall be reviewed with and approved by the Engineer and a record of the inventory shall be submitted to the Engineer for the record.  Without such a record, all systems transferred to the Contractor for maintenance during construction shall be returned at the end of construction in complete, fully operating condition.”

Maintenance and Responsibility During Construction.

Lighting Operation and Maintenance Responsibility.  The scope of work shall include the assumption of responsibility for the continuing operation and maintenance of the existing, proposed, temporary, sign and navigation lighting, or other lighting systems and all appurtenances affected by the work as specified elsewhere herein.  Maintenance of lighting systems is specified elsewhere and will be paid for separately.

The proposed lighting system must be operational prior to opening the roadway to traffic unless temporary lighting exists which is designed and installed to properly illuminate the roadway.

Electrical Infrastructure During Construction.  The scope of work shall include locating and marking the proposed underground infrastructure installed in this contract.

Energy and Demand Charges.  The payment of basic energy and demand charges by the electric utility for existing lighting which remains in service will continue as a responsibility of the Owner, unless otherwise indicated.  Unless otherwise indicated or required by the Engineer duplicate lighting systems (such as temporary lighting and proposed new lighting) shall not be operated simultaneously at the Owner's expense and lighting systems shall not be kept in operation during long daytime periods at the Owner's expense.  Upon written authorization from the Engineer to place a proposed new lighting system in service, whether the system has passed final acceptance or not, (such as to allow temporary lighting to be removed), the Owner will accept responsibility for energy and demand charges for such lighting, effective the date of authorization.  All other energy and demand payments to the utility shall be the responsibility of the Contractor until final acceptance.

Damage to Electrical Systems.  Should damage occur to any existing electrical systems through the Contractor’s operations, the Engineer will designate the repairs as emergency or non-emergency in nature.

Emergency repairs shall be made by the Contractor, or as determined by the Engineer, the Department, or its agent.  Non-emergency repairs shall be performed by the Contractor within six working days following discovery or notification.  All repairs shall be performed in an expeditious manner to assure all electrical systems are operational as soon as possible.  The repairs shall be performed at no additional cost to the Department.

Lighting.  An outage will be considered an emergency when three or more lights on a circuit or three successive lights are not operational.  Knocked down materials, which result in a danger to the motoring public, will be considered an emergency repair.

Temporary aerial multi-conductor cable, with grounded messenger cable, will be permitted if it does not interfere with traffic or other operations, and if the Engineer determines it does not require unacceptable modification to existing installations.

Marking Proposed Locations.  The Contractor shall mark or stake the proposed locations of all poles, cabinets, junction boxes, pull boxes, handholes, cable routes, pavement crossings, and other items pertinent to the work.  A proposed location inspection by the Engineer shall be requested prior to any excavation, construction, or installation work after all proposed installation locations are marked.  Any work installed without location approval is subject to corrective action at no additional cost to the Department.

Inspection of electrical work.  Inspection of electrical work shall be according to Article 105.12 and the following.

Before any splice, tap, or electrical connection is covered in handholes, junction boxes, light poles, or other enclosures, the Contractor shall notify and make available such wiring for the Engineer’s inspection.

Testing.

General. Before final inspection, the electrical work shall be tested.  Tests may be made progressively as parts of the work are completed or may be made when the work is complete.  Tests shall be made in the presence of the Engineer.  Items which fail to test satisfactorily shall be repaired or replaced.  Tests shall include checks of control operation, system voltages, cable insulation, and ground resistance and continuity.

The forms for recording test readings will be available from the Engineer in electronic format.  The Contractor shall provide the Engineer with a written report of all test data including the following:

- Voltage Tests

- Amperage Tests

- Insulation Resistance Tests

- Continuity tests

- Resistance of Grounding Electrodes

- Detector Loop Tests

Lighting systems.  The following tests shall be made.

(1)	Voltage Measurements.  Voltages in the cabinet from phase to phase and phase to neutral, at no load and at full load, shall be measured and recorded.  Voltage readings at the last termination of each circuit shall be measured and recorded.

(2)	Insulation Resistance.  Insulation resistance to ground of each circuit at the cabinet shall be measured and recorded with all loads disconnected. Prior to performance of the insulation resistance test, the Contractor shall remove all fuses within all light pole bases on a circuit to segregate the luminaire loads.

On tests of new cable runs, the readings shall exceed 50 megohms for phase and neutral conductors with a connected load over 20A and shall exceed 100 megohms for conductors with a connected load of 20A or less.

On tests of cable runs which include cables which were existing in service prior to this contract, the resistance readings shall be the same or better than the readings recorded at the maintenance transfer at the beginning of the contract.  Measurements shall be taken with a megohm meter approved by the Engineer.

(3)	Loads.  The current of each circuit, phase main, and neutral shall be measured and recorded.  The Engineer may direct reasonable circuit rearrangement.  The current readings shall be within ten percent of the connected load based on material ratings.

(4)	Ground Continuity.  Resistance of the system ground as taken from the farthest extension of each circuit run from the controller (i.e. check of equipment ground continuity for each circuit) shall be measured and recorded.  Readings shall not exceed 2.0 ohms, regardless of the length of the circuit.

(5)	Resistance of Grounding Electrodes.  Resistance to ground of all grounding electrodes shall be measured and recorded.  Measurements shall be made with a ground tester during dry soil conditions as approved by the Engineer.  Resistance to ground shall not exceed 10 ohms.

Surveillance. The following tests shall be made in addition to the lighting system test above.

(1)	Detector Loops.  Before and after permanently securing the loop in the pavement, the resistance, inductance, resistance to ground, and quality factor for each loop and lead-in circuit shall be tested.

(2)	The loop and lead-in circuit shall have an inductance between 20 and 2500 microhenries.

(3)	The resistance to ground shall be a minimum of 50 megohms under any conditions of weather or moisture.

(4)	The continuity test of the loop and loop lead-in shall not have a resistance greater than two (2) ohms

(5)	The quality factor (Q) shall be 5 or greater.

Loops which fail to test satisfactorily shall be repaired or replaced.

Telecommunication Cable.  Once the telecommunication cable is installed complete with all cable terminations complete the Contractor shall request an end-to-end test.  The Contractor shall request the end-to-end test at least 7 days in advance to the TSC Engineer.  Any lane closures and/or any other safety measures that need to be taken shall be provided for by the Contractor and shall be considered incidental to the cost of this item.  The type of test performed shall be an end-to-end test with Halcyon type equipment transmitting and receiving at each end of the cable.  Each pair shall be tested, and the results shall be recorded and submitted to the Engineer.  If any results don't fall within the requirements set forth in (REA) PE-39, the Contractor shall correct and re-test that cable pair.  Traffic Systems will tolerate only one pair out of every 100 pair of cable that doesn't meet or exceed specifications set forth in (REA) PE-39.

Wireless In-Pavement Detection Systems shall be tested in accordance with the approved testing procedures provided in the catalog cut submittal.

Fiber Optic Systems.

The Contractor shall submit detailed test procedures for approval by the Engineer.  All fibers (terminated and un-terminated) shall be tested bi-directionally at both 1310 nm and 1550 nm with both an Optical Time Domain Reflectometer (OTDR) and a power meter with an optical source.  For testing, intermediate breakout fibers may be concatenated and tested end-to-end.  Any discrepancies between the measured results and these specifications will be resolved to the satisfaction of the Engineer.

Fibers which are not to be terminated shall be tested with a temporary fusion spliced pigtail fiber.   Mechanical splice or bare fiber adapters are not acceptable.

The Contractor shall provide the date, time and location of any tests required by this specification to the Engineer at least 5 working (7 calendar) days before performing the test.  Included with the notification shall be a record drawing of the installed fiber optic cable system.  The drawings shall indicate actual installed routing of the cable, the locations of splices, and locations of cable slack with slack quantities identified.

Upon completion of the cable installation, splicing, and termination, the Contractor shall test all fibers for continuity, events above 0.1 dB, and total attenuation of the cable. The test procedure shall be as follows:

A Certified Technician utilizing an Optical Time Domain Reflectometer (OTDR) and Optical Source/Power Meter shall conduct the installation test.  The test equipment used shall have been calibrated within the last two years.  Documentation shall be provided. The Technician is directed to conduct the test using the standard operating procedures defined by the manufacturer of the test equipment.  All fibers installed shall be tested in both directions.

A fiber ring or fiber box shall be used to connect the OTDR to the fiber optic cable under test at both the launch and receive ends.  The tests shall be conducted at 1310 and 1550 nm for all fibers.

All testing shall be witnessed by the IDOT Engineer, and a copy of the test results (CD ROM or USB Drive) shall be submitted on the same day of the test.  Hardcopies shall be submitted as described herein with copies on CD ROM or USB Drive.

At the completion of the test, the Contractor shall provide copies of the documentation of the test results to the Project Engineer. The test documentation shall be submitted as two bound copies and three CD ROM, or USB drive copies, and shall include the following:

Cable & Fiber Identification:

| - Cable ID | - Operator Name |
| --- | --- |
| - Cable Location - beginning and end point | - Date & Time |
| - Fiber ID, including tube and fiber color | - Setup Parameters |
| - Wavelength | - Range (OTDR) |
| - Pulse width (OTDR) | - Scale (OTDR) |
| - Refractory index (OTDR) | - Setup Option chosen to pass OTDR “dead zone” |

Test Results shall include:

| - OTDR Test results | - Measured Length (Cable Marking) |
| --- | --- |
| - Total Fiber Trace | - Total Length (OTDR) |
| - Splice Loss/Gain | - Optical Source/Power Meter Total Attenuation (dB/km) |
| - Events > 0.10 dB |  |

Sample Power Meter Tabulation:

| Power Meter Measurements (dB) |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Location |  | Fiber No. | Cable Length (km) | A to B |  | B to A |  | Bidirectional Average |  |
| A | B |  |  | 1310 nm | 1550 nm | 1310 nm | 1550 nm | 1310 nm | 1550 nm |
|  |  | 1 |  |  |  |  |  |  |  |
|  |  | 2 |  |  |  |  |  |  |  |
| Maximum Loss |  |  |  |  |  |  |  |  |  |
| Minimum Loss |  |  |  |  |  |  |  |  |  |

The OTDR test results file format must be Bellcore/Telcordia compliant according to GR-196-CORE Issue 2, OTDR Data Standard, GR 196, Revision 1.0, GR 196, Revision 1.1, GR 196, Revision 2.0 (SR-4731) in a “.SOR” file format.  A copy of the test equipment manufacture’s software to read the test files, OTDR and power, shall be provided to the Department.  These results shall also be provided in tabular form, see sample below:

| Sample OTDR Summary |  |  |  |  |
| --- | --- | --- | --- | --- |
| Cable Designation: | TCF-IK-03 | OTDR Location: | Pump Sta. 67 | Date: 1/1/00 |
| Fiber Number | Event Type | Event Location | Event Loss (dB) |  |
|  |  |  | 1310 nm | 1550 nm |
| 1 | Splice | 23500 Ft. | .082 | .078 |
| 1 | Splice | 29000 Ft. | .075 | .063 |
| 2 | Splice | 29000 Ft. | .091 | .082 |
| 3 | Splice | 26000 Ft. | .072 | .061 |
| 3 | Bend | 27000 Ft. | .010 | .009 |

The following shall be the criteria for the acceptance of the cable:

Upon completing all splicing operations for a cable span, the Contractor shall measure the mean bi-directional loss at each splice using an Optical Time Domain Reflectometer.

When splices are made between identical cables (same manufacturer and cable type) the average optical loss of each splice shall not exceed 0.10 dB.  The average is determined by measuring the splice loss in both directions with an OTDR, adding the two readings, and dividing by two.  Testing should be performed for both the 1310 and 1550 nm wavelengths.  No individual splice loss measured in a single direction shall exceed 0.15 dB.

When splices are made between cables containing fibers of different mode field diameters, the average optical loss of each splice shall not exceed 0.50 dB.  The average is determined by measuring the splice loss in both directions with an OTDR, adding the two readings, and dividing by two.  Testing should be performed for both the 1310 and 1550 nm wavelengths.  No individual splice loss measured in a single direction shall exceed 0.6 dB.

The Contractor shall measure the end-to-end attenuation of each fiber, from connector to connector, using an optical power meter and source. This loss shall be measured at from both directions and shall not exceed 0.5 dB per installed kilometer of single mode cable. Measurements shall be made at both 1300 and 1550 nm for single mode cable.

For multimode cable, power meter measurements shall be made at 850 and 1300 nm. The end-to-end attenuation shall not exceed 3.8 dB/installed kilometers at 850nm or 1.8 dB per installed kilometer at 1300nm for multimode fibers.

If the total loss exceeds these specifications, the Contractor shall replace or repair the cable run at the no additional cost to the state, both labor and materials. Elevated attenuation due to exceeding the pulling tension, or any other installation operation, during installation shall require the replacement of the cable run at no additional cost to the State, including labor and materials.

All test results shall be furnished to the Engineer seven working days before the date the inspection is scheduled.

Contract Guarantee.  The Contractor shall provide a written guarantee for all electrical work provided under the contract for a period of six months after the date of acceptance with the following warranties and guarantees.

(a)	The manufacturer’s standard written warranty for each piece of electrical material or apparatus furnished under the contract.  The warranty for light emitting diode (LED) modules, including the maintained minimum luminance, shall cover a minimum of 120 months from the date of delivery.

(b)	The Contractor’s written guarantee that, for a period of six months after the date of final acceptance of the work, all necessary repairs to or replacement of said warranted material or apparatus for reasons not proven to have been caused by negligence on the part of the user or acts of a third party shall be made by the Contractor at no additional cost to the Department.

(c)	The Contractor’s written guarantee for satisfactory operation of all electrical systems furnished and constructed under the contract for a period of six months after final acceptance of the work.

The warranty for an uninterruptable power supply (UPS) shall cover a minimum of two years from date the equipment is placed in operation; however, the batteries of the UPS shall be warranted for full replacement for a minimum of five years.

Record Drawings.  Alterations and additions to the electrical installation made during the execution of the work shall be made on the PDF copy of the as-Let documents using a PDF editor. Hand drawn notations or markups and scanned plans are not acceptable. These drawings shall be updated daily and shall be available for inspection by the Engineer during the work.  The record drawings shall include the following:

- Cover Sheet

- The Electrical Maintenance Contract Management System (EMCMS) location designation, i.e. “L”, “TS”, “S”, “A” number.

- Summary of Quantities, electrical items only

- Legends, Schedules, and Notes

- Plan Sheets

- Final fiber assignment tables

- Pertinent Details

- Single Line Diagrams; electrical, communications, surveillance and fiber optic.

- Other useful information useful to locate and maintain the systems.

Any modifications to the details shall be indicated.  Final quantities used shall be indicated on the Summary of Quantities. Foundation depths used shall also be listed.

As part of the record drawings, the Contractor shall inventory all materials, new or existing, on the project and record information on inventory sheets provided by the Engineer.

The inventory shall include:

- Location of Equipment, including rack, chassis, slot as applicable.

- Designation of Equipment

- Equipment manufacturer

- Equipment model number

- Equipment Version Number

- Equipment Configuration

  - Addressing, IP or other

  - Settings, hardware or programming

- Equipment Serial Number

The following electronic inventory forms are available from the Engineer:

- Lighting Controller Inventory

- Lighting Inventory

- Light Tower Inspection Checklist

- ITS Location Inventory

The information shall be entered in the forms; handwritten entries will not be acceptable; except for signatures.  Electronic file shall also be included in the documentation.

When the work is complete, and seven days before the request for a final inspection, the set of contract drawings, marked “RECORD DRAWINGS”, shall be submitted to the Engineer for review and approval and shall be stamped with the date and the signature of the Contractor’s supervising Engineer or Electrician.  The record drawings shall be submitted in PDF format via a mutually agreed to electronic format for review and approval.

In addition to the record drawings, PDF copies of the final catalog cuts which have been Approved and Approved as Noted with applicable follow-up shall be submitted along with the record drawings.  The PDF files shall clearly indicate either by filename or PDF table of contents (bookmarks) the respective pay item number.  Specific part or model numbers of items which have been selected shall be clearly visible.

If the Electric Service is new or modified, documentation as required in the Electric Utility Service Connection shall be submitted.

During the Final Inspection, the Contractor shall provide three sets of electronically produced drawings in a moisture proof pouch to be kept on the inside door of the controller cabinet or other location approved by the Engineer. These drawings shall show the final as-built circuit orientation(s) of the project in the form of a single line diagram with all equipment designations and clearly identified.

Final documentation shall be submitted as a complete submittal package, i.e. record drawings, test results, inventory, etc. shall be submitted at the same time.  Partial piecemeal submittals will be rejected without review.

A total of three hardcopies and two CD-ROMs or USB Drives of the final documentation shall be submitted.  The identical material shall also be submitted in the same manner as the catalog cut submittals utilizing the following final documentation pay item numbers:

| Pay Code | Description | Discipline |
| --- | --- | --- |
| FDLRD000 | Record Drawings - Lighting | Lighting |
| FDSRD000 | Record Drawings - Surveillance | Surveillance |
| FDTRD000 | Record Drawings - Traffic Signal | Traffic Signal |
| FDIRD000 | Record Drawings - ITS | ITS |
| FDLCC000 | Catalog Cuts - Lighting | Lighting |
| FDSCC000 | Catalog Cuts – Surveillance | Surveillance |
| FDTCC000 | Catalog Cuts – Traffic Signal | Traffic Signal |
| FDICC000 | Catalog Cuts - ITS | ITS |
| FDLWL000 | Warranty - Lighting | Lighting |
| FDSWL000 | Warranty - Surveillance | Surveillance |
| FDTWL000 | Warranty - Traffic Signal | Traffic Signal |
| FDIWL000 | Warranty - ITS | ITS |
| FDLTR000 | Test Results - Lighting | Lighting |
| FDSTR000 | Test Results - Surveillance | Surveillance |
| FDTTR000 | Test Results - Traffic Signal | Traffic Signal |
| FDITR000 | Test Results - ITS | ITS |
| FDLINV00 | Inventory - Lighting | Lighting |
| FDSINV00 | Inventory - Surveillance | Surveillance |
| FDTINV00 | Inventory - Traffic Signal | Traffic Signal |
| FDIINV00 | Inventory - ITS | ITS |
| FDLGPS00 | GPS - Lighting | Lighting |
| FDSGPS00 | GPS - Surveillance | Surveillance |
| FDTGPS00 | GPS - Traffic Signal | Traffic Signal |
| FDIGPS00 | GPS - ITS | ITS |
| FDLES00 | Electric Service - Lighting | Lighting |
| FDSES00 | Electric Service - Surveillance | Surveillance |
| FDTES00 | Electric Service - Traffic Signal | Traffic Signal |
| FDIES00 | Electric Service - ITS | ITS |

Record Drawings shall include Marked up plans, controller info, Electric Service Info, Equipment Settings, Manuals, Wiring Diagrams for each discipline.

Test results shall be all electrical test results, fiber optic OTDR, and Fiber Optic power meter as applicable for each discipline.

GPS Documentation.  In addition to the specified record drawings, the Contactor shall record GPS coordinates of the following electrical components being installed, modified or being affected in other ways by this contract:

- All light poles and light towers.

- Handholes and vaults.

- Junction Boxes

- Conduit roadway crossings.

- Controllers.

- Control Buildings.

- Structures with electrical connections, i.e. DMS, lighted signs.

- Electric Service locations.

- CCTV Camera installations.

- Roadway Surveillance installations.

- Fiber Optic Splice Locations.

- Fiber Optic Cables.  Coordinates shall be recorded along each fiber optic cable route every 200 feet.

- Fiber Optic Utility Markers

- All fiber optic slack locations shall be identified with quantity of slack cable included.  When sequential cable markings are available, those markings shall be documented as cable marking into enclosure and marking out of enclosure.

- All wireless in-pavement vehicle detectors

Datum to be used shall be North American 1983.

Data shall be provided electronically.  The electronic format shall be compatible with MS Excel.  Latitude and Longitude shall be in decimal degrees with a minimum of 6 decimal places.   Each coordinate shall have the following information:

- District

- Description of item

- Designation

- Use

- Approximate station

- Contract Number

- Date

- Owner

- Latitude

- Longitude

- Comments

A spreadsheet template will be available from the Engineer for use by the Contractor.

Accuracy.  Data collected is to be mapping grade.  A handheld mapping grade GPS device shall be used for the data collection.  The receiver shall support differential correction and data shall have minimum 5 meter accuracy after post processing.

GPS receivers integrated into cellular communication devices, recreational and automotive GPS devices are not acceptable.

The GPS shall be the product of an established major GPS manufacturer having been in the business for a minimum of 6 years.”

The documents on the CD ROM, or USB Drive shall be organized by the Electrical Maintenance Contract Management System (EMCMS) location designation.  If multiple EMCMS locations are within the contract, separate folders shall be utilized for each location as follows:

Extraneous information not pertaining to the specific EMCMS location shall not be included in that particular folder and sub-folder.

The inspection will not be made until after the delivery of acceptable record drawings, specified certifications, and the required guarantees.

The Final Acceptance Documentation Checklist shall be completed and is contained elsewhere herein.

If CD’s are used they shall be labeled as illustrated in the CD Label Template contained herein.

Acceptance.  Acceptance of electrical work will be given at the time when the Department assumes the responsibility to protect and maintain the work according to Article 107.30 or at the time of final inspection.

When the electrical work is complete, tested, and fully operational, the Contractor shall schedule an inspection for acceptance with the Engineer no less than seven working days prior to the desired inspection date.  The Contractor shall furnish the necessary labor and equipment to make the inspection.

A written record of the test readings taken by the Contractor according to Article 801.13 shall be furnished to the Engineer seven working days before the date the inspection is scheduled.  Inspection will not be made until after the delivery of acceptable record drawings, specified certifications, and the required guarantees.

Final Acceptance Documentation Checklist

| LOCATION |  |
| --- | --- |
| Route | Common Name |
| Limits | Section |
| Contract # | County |
| Controller Designation(s) | EMC Database Location Number(s) |

| ITEM | Contractor (Verify) | Resident Engineer (Verify) |
| --- | --- | --- |
| Record Drawings -Three hardcopies (11” x 17”) -PDFs as required elsewhere |  |  |
| Field Inspection Tests -Voltage -Amperage -Cable Insulation Resistance -Continuity -Controller Ground Rod Resistance (Three Hardcopies & PDFs as required) |  |  |
| GPS Coordinates -Excel file (Check Special Provisions, Excel file required.) |  |  |
| Job Warranty Letter (Three Hardcopies & PDFs as required) |  |  |
| Catalog Cut Submittals -Approved & Approved as Noted (PDFs as required) |  |  |
| Lighting Inventory Form (Three Hardcopies & PDFs as required) |  |  |
| Lighting Controller Inventory Form (Three Hardcopies & PDFs as required) |  |  |
| Electric Service Documentation (Three Hardcopies & PDFs as required) |  |  |
| Light Tower Inspection Form (If applicable, Three Hardcopies & PDFs as required) |  |  |

Three Hardcopies & PDFs as required shall be submitted for all items above.  If a CD ROM is used it shall be labeled as shown in the example contained herein.

General Notes:

Record Drawings – The record drawings should contain contract cover sheet, summary of quantities showing all lighting pay item sheets, proposed lighting plans and lighting detail sheets.  Submit hardcopies shall be 11” x 17” size.  Temporary lighting plans and removal lighting plans should not be part of the set.

Field Inspection Tests – Testing should be done for proposed cables.  Testing shall be per standard specifications.  Forms shall be neatly filled out.

GPS Coordinates – Check special provisions “General Electrical Requirements”.  Submit electronic “EXCEL” file.

Job Warranty Letter – See standard specifications.

Cutsheet Submittal – See special provisions “General Electrical Requirements”.  Scan Approved and Approved as Noted cutsheets.

Lighting Inventory Form – Inventory form should include only proposed light poles, proposed light towers, proposed combination (traffic/light pole) lighting and proposed underpass luminaires.

Lighting Controller Inventory Form – Form should be filled out for only proposed lighting controllers.

Light Tower Safety Inspection Form – Form should be filled out for each proposed light tower.

CD LABEL FORMAT TEMPLATE.

Label must be printed; hand written labels are unacceptable and will be rejected.

Contract: 60X23

Letting: 1/20/12

Route: FAU 123 (IL 83)

Limits: IL64 to IL56

Section: 123N-XYZ(L)TS

County: DuPage

Acme Construction

Submittal Date

2/29/14

Items

Record Drawings

Final Approved Submittals

Test Results

Inventory

Warranty Letters