## Uninterruptible Power Supply

Revised 6/8/2023

This work shall consist of furnishing and installing an uninterruptible power supply, hereinafter referred to as the "UPS", in the local controller cabinet.

The UPS shall be capable of keeping the signals running green, yellow and red during periods of utility power failure. The UPS shall meet the following requirements:

1.	Maintain power for a minimum of 60 minutes upon power failure.

2.	Electrical inputs:

AC Input Voltage:……..	95-135 Volts

AC Input Current:……..	30 Amps Max

Frequency:…………….. Auto-sensing

3.	Electrical outputs:

AC Output Voltage: .........+/- 10% over input voltage range

Current:........................... 9.2A nominal

Power at 50°C:................1100W/VA

4. 	Display:

Full graphic LCD, 480x272 pixels, Resistive touch screen

5.    Dimensions:

Inches:............................5.22H x 15.5W x 8.75D

6.	A plug type connection (if possible) should output to the controller's "D" panel when the UPS battery is about to fail.

7. 	A heater shall be provided either internally or externally to maintain an adequate operation temperature for the UPS.  The batteries shall be kept charged by a balanced charging system.

8.	A bypass relay shall be provided to prevent flash failure when commercial power is available.

Basis of Payment.  This work will be paid for at the contract unit price each for UNINTER RUPTIBLE POWER SUPPLY, which price shall be payment in full for furnishing and installing the UPS complete with necessary connections for proper operation at the local controller intersection.