## Fiber Optic Cable Innerduct

Effective: October 1, 2014

1.	Description.

This item shall consist of furnishing, installing, splicing, connecting and demonstrating continuity of fiber optic cable innerduct of sizes specified herein and as shown on the contract drawings.  The innerduct shall be High Density Polyethylene.

3.	Materials.

3.1	General:

The duct shall be a spiral ribbed plastic duct which is intended for underground use and which can be manufactured and coiled or reeled in continuous transportable lengths and uncoiled for further processing and/or installation without adversely affecting its properties of performance.  The ribbed duct shall have internally designed longitudinal ribs for reduced pulling frictions and increased lubrication effectiveness

The duct shall be made of high density polyethylene which shall meet the requirements of ASTM D 3035.  The innerduct material shall be composed of high density polyethylene meeting the requirements of PE334470E/C as defined in ASTM D3350.

Submittal information shall demonstrate compliance with the details of these requirements.

3.2	Dimensions:

Duct dimensions shall conform to the standards listed in ASTM D3035, SDR-11.  Submittal information shall demonstrate compliance with these requirements.

| Nominal Size (Diameter) | Inside Diameter (minimum) | Outside Diameter (Average) | Wall Thickness (Min.) | Bend Radius (minimum) | Pull Strength | Weight Average (lbs/100ft.) |
| --- | --- | --- | --- | --- | --- | --- |
| 1” | 1.030” | 1.315” | 0.120” | 14” | 500 | 19 |
| 1.25” | 1.313” | 1.660” | 0.151” | 17” | 750 | 31 |
| 1.5” | 1.506” | 1.900” | 0.173” | 19” | 1000 | 40 |
| 2” | 1.885” | 2.375” | 0.216” | 24” | 1600 | 60 |

3.3	Marking:

As specified in NEMA Standard Publication No. TC-7, the duct shall be clearly and durably marked at least every 10 feet with the material designation (HDPE for high density polyethylene), nominal size of the duct, and the name and/or trademark of the manufacturer.

3.4	Color:

Innerduct shall be colored as follows or as directed by the Engineer.

| Usage Designation | Color |
| --- | --- |
| Fiber Optic Trunk Cable (Ducts containing cables of 96 fibers) | Orange |
| Fiber Optic Distribution Cable (Ducts containing cables of 12, 6 or 4 fibers and 96 fiber ducts designated as distribution fibers) | Blue |

4.	Installation.

4.1	Pulling Tension.

Pulling tension of the duct shall be monitored throughout the pull and pulling tension shall not exceed those listed in the table or the specific manufacturer maximum pulling tensions as indicated in the catalog cut submittals.  Failure to monitor the pulling tension will result is non-payment of that particular duct span and the span may be reinstalled with new duct at no additional cost to the State.  Lubricants used shall be compatible with the duct.

4.2	Junction boxes.

Where duct passes through junction and/or pull boxes, the duct shall remain continuous unless a break is specifically indicated in the plans or as directed by the Engineer.

4.3	Handholes and Communications Vaults.

Where duct passes through handholes or vaults, the duct shall be looped uncut within the handhole unless otherwise indicated on the Plans or directed by the Engineer.

Bends.

Minimum bending radius shall be in accordance with the above table or the manufacturer's recommended radius, whichever is larger.  Bends shall be made so that the duct will not be damaged and the internal diameter of the duct will not be effectively reduced.  The degrees of bend in one duct run shall not exceed 360º between termination points.

4.4	In Trench

Where duct is installed in trench, it shall be placed in the bottom of the trench after all loose stones have been removed and all protruding stones have been removed or covered with backfill material as directed by the Engineer.

Where duct is shown to be installed in trench, it shall be installed at a depth not less than 30 inches unless otherwise indicated or specifically directed by the Engineer.

The inner duct may be plowed into place.  Unless otherwise indicated or specifically approved by the Engineer, plowing of inner duct shall lay the duct in place and shall not pull the duct through the length of the cut behind a bullet-nose mandrel or similar apparatus.  In all cases, plowing operations shall be non-injurious to the duct.

4.5	In Raceway

Where duct is installed in raceways, lubricating compounds shall be used where necessary to assure smooth installation.

4.6	Encased in Concrete

Concrete shall be class SI complying with Section 720 of the Standard Specifications.

Steel Reinforcement Bars.  Steel reinforcement bars shall comply with Section 706.10 of the Standard Specifications.

Underground concrete-encased conduit shall be supported on interlocking plastic spacers specifically designed for the purpose spaced along the length of the run as recommended by the manufacturer.  Spacing between raceways within a common duct dank shall be not less than 2 inches.  The interlocking spacers shall be used at a minimum interval of 8 ft.

Concrete cover overall shall not be less than 3 inches all around the encased run.  Space below the conduit, and concrete fill shall be assured.  Care shall be exercised during concrete placement to assure that there are no voids, so that spacers are undisturbed, and so that conduit joints stay secure and unbroken.  Concrete shall be deflected during placement to minimize the possible damage to or movement of the conduits.

Conduit encased in concrete shall have steel reinforcing where installed below roadway or other paved vehicle areas (including shoulder) and the reinforcement shall extend not less than 5 feet additional from the edge of pavement unless otherwise indicated.  Steel reinforcement shall not be less than No. 4 bars at corners and otherwise spaced on 12-inch centers, tied with No. 4 bars on 12-inch centers.

The Engineer shall examine all conduit joints for compliance with section 5 of this specification before concrete is poured.

4.7	Embedded

Conduit embedded in structure shall be supported on interlocking plastic spacers specifically designed for the purpose spaced along the length of the run as recommended by the manufacturer.  Spacing between raceways within a common structure shall be not less than 2 inches.  The interlocking spacers shall be used at a minimum interval of 8 ft.

Concrete cover overall shall not be less than 3 inches all around the embedded run.  Space below the conduit, and concrete fill shall be assured.  Care shall be exercised during concrete placement to assure that there are no voids, so that spacers are undisturbed, and so that conduit joints stay secure and unbroken.  Concrete shall be deflected during placement to minimize the possible damage to or movement of the conduits.

The Engineer shall examine all conduit joints for compliance with section 5 of this specification before concrete is poured.

5.	Joints

5.1	All HDPE duct to HDPE duct joints shall be made with an approved duct fusion splicing device.

5.2	HDPE coilable non-metallic conduit to non-HDPE coilable non-metallic conduit joints shall be either made with an approved mechanical connector or with a chemical compound.  Both methods must be specifically designed for joining HDPE coilable non-metallic conduit.  Minimum pullout force for the chemical compound shall be as listed in the following table.

| Nominal Size |  | Pullout Force |  |
| --- | --- | --- | --- |
| mm | in | N | Lbs |
| 31.75 | 1.25 | 2400 | 540 |
| 38.1 | 1.50 | 2535 | 570 |
| 50.8 | 2.0 | 3335 | 750 |
| 63.5 | 2.5 | 4445 | 1,000 |
| 76.2 | 3.0 | 6225 | 1,400 |
| 101.6 | 4.0 | 8890 | 2,000 |

7.	Measurement.

The duct shall be measured for payment in linear feet in place as described herein.  Measurements shall be made in straight lines between horizontal changes in direction between the centers of the terminating points (poles, cabinets, junction boxes).  Vertical measurement of the duct shall be as follows:

For runs terminating at junction boxes and/or control cabinets, the vertical measurement shall be taken from the bottom of the trench, or horizontal raceway, to a point 18-inches beyond the center of the junction box or control cabinet.

For runs terminating at poles, the vertical measure shall be taken from the bottom of the trench, or horizontal raceway, to a point 18-inch beyond the center of the light pole handhole regardless of light pole mounting method

Innerduct installed in excess of the limits describes herein shall not be paid for.

8.	Basis of Payment.

This item will be paid for at the contract unit price per foot installed for INNERDUCT, of the size of duct as indicated, which shall be payment in full for all material and work as specified herein.