# STORM SEWER ADJACENT TO OR CROSSING WATER MAIN (D1)

Effective: February 1, 1996

Revised: January 1, 2007

This work consists of constructing storm sewer adjacent to or crossing a water main, at the locations shown on the plans.  The material and installation requirements shall be according to the latest edition of the “Standard Specifications for Water and Sewer Main Construction in Illinois”, and the applicable portions of Section 550 of the Standard Specifications; which may include concrete collars and encasing pipe with seals if required.

Pipe materials shall meet the requirements of Sections 40 and 41-2.01 of the “Standard Specifications for Water and Sewer Main Construction in Illinois”, except PVC pipe will not be allowed.  Ductile-Iron pipe shall meet the minimum requirements for Thickness Class 50.

Encasing of standard type storm sewer, according to the details for “Water and Sewer Separation Requirements (Vertical Separation)” in the “STANDARD DRAWINGS” Division of the “Standard Specifications for Water and Sewer Main Construction in Illinois”, may be used for storm sewers crossing water mains.

Basis of Payment: This work will be paid according to Article 550.10 of the Standard Specifications, except the pay item shall be STORM SEWER (WATER MAIN REQUIREMENTS), of the diameter specified.

X0322033	STORM SEWER (WATER MAIN REQUIREMENTS) 12 INCH	FOOT

MX030063	STORM SEWER (WATER MAIN REQUIREMENTS) 300 MM	METER

DESIGNER’S NOTES:

- This item of work is to be used when both of the following conditions exist:

1. Horizontal separation

Storm Sewer is located closer than 10 feet (3 m) to a water main.

2. Vertical separation.

A. Storm Sewer crosses over a water main.

B. Storm Sewer is adjacent to or crosses under a water main and the  separation is less than 18 inches  (450 mm).

- All required locations must be shown in the plans.

h:\sp\des\5501234r.doc