## Light Pole Breakaway Device

Effective:  November 1, 2025

Description.

This work shall consist of furnishing and installing a breakaway device. The device may be either a transformer base or a set of four breakaway couplings at the Contractor’s discretion. However, all breakaway devices for the contract must be of the same type; mixing transformer bases and couplings in the same contract is not allowed.

Materials.

Breakaway Couplings

General.

Certification shall be submitted from the supplier that the device used under the conditions of the particular design meets the AASHTO breakaway specification. Certification shall include test results performed by the manufacturer, supplier or others. If test results have been previously approved by a letter from the FHWA, a copy of the approval letter from FHWA should accompany the certification. The coupling shall not alter the bolt circle of the pole. The breakaway device shall be vandal resistant and shall not adversely affect the light pole installation and maintenance or decrease the resistance of the light pole to non-collision type of design loading. The breakaway device shall be field attachable and detachable.

Breakaway Coupling Cover.

The breakaway device shall have a cover enclosing the space between the bottom of the pole base plate and the foundation consisting of a Type 304 stainless steel wire cloth mesh with a maximum opening of 1/4 in. (6 mm) and a minimum wire diameter of AWG No. 16 (1.6 mm) with a minimum lap of 6 in. (150 mm) to enclose the void between the pole base and the foundation. The lap shall be tied together with Type 304 stainless steel wire ties. When specified, an aluminum skirt cover shall be provided over the wire cloth. The aluminum skirt shall be made of ASTM B209 Alloy 3003-H14 or 5052-H32, 0.0625 in. (1.6 mm) thick minimum. The enclosure shall fit snugly around the wire cloth and breakaway devices between the bottom face of the pole base plate and the top of the foundation. Vertical or horizontal movement of the cover will not be acceptable.

Transformer Base.

General.

The breakaway device shall be a cast and welded aluminum transformer base type pole base. The breakaway device shall have a listing of approval by FHWA to AASHTO breakaway requirements. This shall require compliance to AASHTO “Specifications for Structural Supports for Highway Signs, Luminaires, and Traffic Signals, Sixth Edition, 2013”. Submittal information shall document the approval listing.

The device shall be approximately 17 in. (430 mm) high or approximately 9 in. (230 mm) high and shall have a large fiberglass or polyethylene access door of a color to match the base finish which shall be held in place with a button-type tamper resistant stainless-steel screw or other means approved by the Engineer.

The 17-inch high transformer base cannot be installed on metal helix foundations.

Bolt Circle Size.

The transformer base shall come in two standard bolt circles.

11.5 in. (290 mm) Pole Bolt Circle Devices. Breakaway devices for poles having nominal 11.5 in. (290 mm) bolt circles shall accommodate bottom (foundation) bolt circles ranging roughly 10 to 12 in. (255 to 300 mm) and shall accommodate top (pole) bolt circles ranging roughly 10.5 to 12 in. (265 to 300 mm).

15 in. (380 mm) Pole Bolt Circle Devices. The bottom foundation bolt circle shall have a range of 15 to 17 in. (380 to 430 mm) and shall accommodate top (pole) bolt circles having a range of 13 to 15 in. (330 to 380 mm).

Access door.

The polyethylene access door shall be fabricated from a high-density polyethylene. The door shall withstand temperature extremes of -76 to 150°F (-60 to 65°C). Ultraviolet light inhibitors shall also be incorporated into the door material. The door shall be reinforced and have tabs to lock into the transformer base door frame.

The appearance of the breakaway device shall be of such general configuration as not to detract from the aesthetic value of the light pole. The device shall have finish that matches the finish of the pole.

Installation.

All entryway points created using breakaway devices shall be permanently and completely sealed against rodent entry. This includes the pole base plate and foundation plate openings, elongated holes for anchor rods, the opening below the pole base plate, and the wiring windows in both steel and concrete foundations. Where breakaway couplings are used in conjunction with steel foundations, the Contractor shall match the plate sizes to seal out rodents between the foundation and pole base. Breakaway devices are not allowed on bridge parapets, barrier walls, or pedestrian conflict areas, and are not required behind guardrail. The Contractor shall verify that the loading of the pole, arm(s), luminaire(s), banner(s), and appurtenances does not exceed the capacity of the breakaway device.

Transformer Base.

The transformer base shall be installed level and flush with the foundation without the use of leveling washers or shims according to the manufacturer’s installation procedures. The anchor rods shall be inserted full depth into the slotted holes of the transformer base. The transformer base shall be installed with access door aligned with light pole handhole. All nuts, bolts, washers, and lock washers required to complete the installation of the transformer base shall be included. A minimum of two thread pitches shall extend beyond the top surface of the nut.

Breakaway Couplings.

The breakaway couplings shall be coordinated to match anchor rod size. The breakaway coupling shall be installed on the anchor rod according to the manufacturer’s recommendations and fully coordinated with the foundation. When used with a metal foundation, a nut shall be installed under the foundation plate on the stud bolt to prevent it from backing out of the breakaway coupling. The coupling installation shall not be used to level the pole base in lieu of a level foundation. The screen shall be tied back on itself and secured with stainless steel wire ties. The screen shall fit tightly and shall completely fill all openings including the voids in the bottom of the pole base

Method of Measurement.

Transformer bases used for breakaway devices will be measured for payment as each, breakaway couplings will be measured as each, for a set of four couplings.

Basis of Payment.

This work will be paid for at the contract unit price per each for LIGHT POLE BREAKAWAY DEVICE.