## Lighting Controller, Radio Control, Duplex Console Type, With SCADA

Effective:  January 1, 2012

Description:  This work shall consist of furnishing and installing a roadway lighting electrical control cabinet with radio control complete with foundation and wiring for the control of highway lighting.

General.  The completed controller shall be an Industrial Control Panel under UL 508, and shall be suitable for use as service equipment

Double Door Enclosure.

Cabinet.  The cabinet shall be of the dimensions shown on the plans and fabricated from 1/8 in. (3 mm) thick aluminum alloy No. 3003-H14.  The cabinet shall comply with ANSI C 33.71 and UL 50 and be reinforced with aluminum angles.

Doors.  The doors shall have stainless steel hinges.  The door handle shall be stainless steel, a minimum diameter of 1/2 in. (13 mm) and be furnished with a rain and ice resistant lock.  The doors shall be gasketed to exclude the entry of moisture, dirt, and insects.  A linkage-arm system, of simple construction, shall be attached to the cabinet doors to allow securing in a wide open position during field operations.

Insulation.  When specified, the interior compartment shall be insulated on the inside of the sides, back, top, bottom, and inside of the doors with 1 in. (25 mm) thick polyisocyanurate rigid foam insulation board.  The foam board shall have foil facers on each side.  The side facing the interior of the cabinet shall have a white tinted foil facer with a satin finish.  The insulation shall have a minimum aged thermal resistance (R-value) of 8 at a 40°F (4°C) mean temperature.  The insulation shall comply with Federal Specification HH-I-1972/1, Class 2.

Mounting.  The cabinet shall be mounted as indicated on the plans.

Work Pad.  Except where the cabinet is facing a sidewalk, a poured, 4 in. (100 mm) thick concrete pad, not less than 48 in. (1.2 m) square shall be provided in front of the cabinet.

Finish.  All aluminum enclosures shall be finished.

Surface Preparation:  The cabinet, doors and all other parts to be painted will be submerged in each tank of a 3 step iron phosphate conversion technique.  After phosphatizing the parts shall be passed through an oven and baked to eliminate any moisture.

Finish coat:  Shall be polyester powder paint applied electrostatically to a minimum thickness of 2 mils and baked at 375°F for 20 minutes.

The color of the finish paint shall be ANSI Standard No. 70 Sky Gray or as specified by the Engineer.

The finish shall be applied according to the paint manufacturer’s recommendations and the manufacturer shall certify, in writing, to the Department, that the finish has been applied properly.

Submittal data submitted for approval shall address the requirement for the paint manufacturer’s certification and shall include a standard, single source paint warranty by the paint manufacturer of the controller manufacturer to the Department.

Identification.  The cabinet door shall have a stainless steel name plate of the dimensions and engraving indicated on the plans.  An identification decal shall also be installed on the back of the cabinet as specified elsewhere herein.

Control Components.

Time Switch.  When specified, each controller shall have an electric time switch for automatic control of highway lighting circuits operating on a daily schedule having a fixed relation to sunrise and sunset.  Turn-on and Turn-off times shall be adjustable ± 45 minutes from sunrise and sunset.  All settings shall be field adjustable without special tools.  Complete installation instructions, details on wiring connections, and information on time setting, manual operation, and necessary adjustments shall be furnished with each time switch.

The time switch shall be a microprocessor-based two channel controller with astronomic functions on both channels.  The latitude shall be adjustable from ten to 60 degrees in the Northern hemisphere.  Latitude changes shall be user  ettable without the use of special tools.

The time switch shall be programmable in an AM/PM format, with a resolution of one minute or better.  The time switch shall automatically adjust for daylight saving time and have automatic leap year correction and operate on 240 V AC without the use of an additional transformer.

A battery backup shall be integral with the controller and shall use a nickel-cadmium battery.  The battery backup shall provide power to the controller memory for a minimum of 72 hours in the event of power failures.

The published operating temperature range of the time switch shall be from 86 to 158°F (-30 to 70°C).

The time switch output relay contacts shall be rated sufficiently to handle the inrush current of two 200 A contactors.  The time switch shall have a NEMA Type 1 enclosure as a minimum.  The time switch programming instructions shall be moisture proof and permanently affixed to the time switch or as otherwise approved by the Engineer.

Circuit Breakers.

All feeders, branch circuits, and auxiliary and control circuits shall have overcurrent protection.  The overcurrent protection shall be by means of circuit breakers.

Circuit breakers shall be standard UL listed molded case, thermal-magnetic bolt-on type circuit breakers with trip free indicating handles.

240 V circuit breakers shall have a UL listed interrupting rating of not less than 10,000 rms symmetrical amperes at rated circuit voltage for which the breaker is applied.  480 V applications shall have a UL listed interrupting rating of not less than 14,000 rms symmetrical amperes at rated circuit voltage.

Multi-pole circuit breakers larger than 100 A size shall have adjustable magnetic trip settings.

The number of branch circuit breakers shall be as indicated on the Control Cabinet detail drawing or as indicated in the lighting system wiring diagram which ever is greater plus two spare circuit breakers.

Contactors.

Contactors shall be electrically operated, mechanically held as specified, with the number of poles required for the service and with operating coil voltage as indicated.  The contactor shall have an in-line drive operating mechanism.  Ampere rating of contactors shall be not less than required for the duty shown and shall otherwise be rated as indicated.

Contactors shall be complete with a non-conducting inorganic, non-asbestos subpanel for mounting.

Mechanically held contactors shall be complete with coil clearing contacts to interrupt current through the coil once the contactor is held in position.

The main contactor contacts shall be the double break, silver to silver type.  They shall be spring loaded and provide a wiping action when opening and closing.  The contacts shall be renewable from the front panel, self aligning, and protected by auxiliary arcing contacts.

The line and load terminals shall be pressure type terminals of copper construction and of the proper size for the ampere rating of the contactor.

A lever for manual operation shall be incorporated in the mechanically held contactor.  Protection from accidental contact with current carrying parts when operating the contactor manually shall be provided.

The contactor operating coil shall operate at phase to neutral voltage.  Single phase contactors shall be two pole devices with continuous rating for the amperage selected per pole.

Open and closed positions for mechanically held contactors shall be clearly indicated and labeled in permanent manner as approved by the Engineer.

Auto/Manual Switches.  The cabinet shall be equipped with automatic and manual operating controls via two, single pole double throw switches, one being a maintained-contact manual-automatic selector switch and one being a momentary-contact manual on-off switch with a center rest position.  Both switches shall be premium specification grade, rated for the applied duty but not less than 20 A at 240 V and each shall be mounted in a 4 in. (100 mm) square box with cover.

The control circuit shall have overcurrent protection as indicated and as required by NEC requirements.

Ground & Neutral Bus Bars.

Separate ground and neutral bus bars shall be provided.  The ground bus bar shall be copper, mounted on the equipment panel, fitted with 22 connectors of the type shown on the plans, as a minimum.  The neutral bar shall be similar.  The heads of connector screws shall be painted white for neutral bar connectors and green for ground bar connectors.

Interior Lighting, Receptacle and CCTV power.

The cabinet shall have an auxiliary device circuit at 120 V single phase to supply a convenience receptacle, cabinet light and a dedicated 120v circuit for CCTV camera power indicated in the plans.  Where 120 V is not available directly from the service voltage, an outdoor dry type step-down transformer not less than 2 KVA shall be provided as described elsewhere herein.

The auxiliary circuit, including transformer primary and secondary, shall have overcurrent protection according to NEC requirements.

The interior, 60 W incandescent lighting fixture of the enclosed-and-gasketed type, shall be switched from a single pole, single throw, 20 A switch.  The switch shall be premium specification grade in a suitable 4 in. (100 mm) box with a cover.

A 20 A duplex receptacle, ground fault interrupting, premium specification grade shall be furnished in a 4 in. (100 mm) square box with cover, for 120 V auxiliary use.

Surge Arrester.

The control circuit in the cabinet shall be protected by a surge arrester meeting the requirements of Article 1065.02.

Wiring and Identification.

Power wiring within the cabinet shall be of the size specified for the corresponding service conductors and branch circuits and shall be rated RHH/RHW, 600 V.

Control and auxiliary circuit wiring shall be rated RHH/RHW or MTW with jacket, 600 V.

All power and control wiring shall be stranded copper.  When specified all wiring shall be tagged with self-sticking cable markers.  When the contract drawings do not specifically indicate assigned wire designations, the manufacturer shall assign wire designations and indicate them on the shop drawings.

All switches, controls and the like shall be identified both as to function and position (as applicable) by means of engraved two color nameplates attached with screws, or where nameplate are not possible in the judgement of the Engineer, by the use of cloth-backed adhesive labels as approved by the Engineer.

The cabinet with all of its electrical components and parts shall be assembled in a neat orderly fashion.  All of the electrical cables shall be installed in a trim, neat, professional manner.  The cables shall be trained in straight horizontal and vertical directions and be parallel, next to, and adjacent to other cables whenever possible.

Transformer, General Purpose.

The transformer shall be dry type and weatherproof so that it may be installed indoors or outdoors without additional housing.  It shall have an enclosure for splices with provisions for weather tight conduit connections.

The transformer shall have four taps on the primary side, one at 2 1/2 percent, one at 5 percent, one at 7 1/2 percent and one at ten percent below rated voltage.

Insulation shall be Class F or Class H.  The transformer shall meet the applicable ASA and IEEE standards.

Mounting and back plates shall be of Aluminum Alloy 2024, 3003 or 6061.  Bolts, nuts and washers shall be of Series 300 stainless steel.  Bolts shall have hexheads.  Nuts shall be hexagon and self locking.  Washers shall be of the flat type.

Radio Control Equipment.

Receiver - Decoder: The radio control module consists of a radio receiver, digital decoder, and an output interface which allows centralized remote radio control of the lighting controller turn-on and turn-off functions.  The radio control module must be capable of operation consistent with the existing radio control system, a Motorola SCADA Central Station.

The existing control system currently operates over 250 discrete lighting controllers via a securely coded proprietary data scheme.  For this reason, the control module must consist of a Motorola ACE 3600 Modular Remote Unit, model F 7563, (small housing), with no less than the following options:

| Motorola Designation | Description |
| --- | --- |
| F 7563 (VHF), F 7564 (UHF) | ACE 3600 CPU * |
| V 245 | Mixed I/O |
| V 261 | 240 VAC Power Supply w/charger |
| Z 857AA | Surge Protection |

* Includes (1) three slot frame, (1) ACE 3600 CPU plus firmware, (1) mixed I/O Module, (1) VHF or UHF (as directed by the Engineer) CDM 750 Radio with FSK Radio Interface, port 3 (1) AC Power Supply with Charger, (1) 6.5 Ah battery, installed in a 15“ X 15” X 8.26” NEMA 4X/IP 56 painted metal enclosure with instruction manual.

The manufacturer's designation by no means relieves the Contractor of providing a fully functional radio system as described herein.

A 120/240 to 24VAC step down transformer shall be included for the SCADA system.

The Radio Control Module shall be programmed for the following operational parameters:

- Transceiver Frequency: To be specified by the Engineer

- Receive Frequency: To be specified by the Engineer

- Communications Failure Preset:  Normally Open

- Individual Station address:  To be specified by the Engineer

Antenna.  The antenna shall be thick mount up to ½” mounting surface mounted by screw adapter (no magnet mounts).  The low profile antenna mount shall be equivalent to Antenex – MABT8XNSI antenna Mount Low Profile.  Accompanying antenna shall be equivalent to Antenex – B132 (Broad Band – VHF/UHF ¼ wave 150-928 MHz.  Accompanying cable shall be equivalent to Antenex-RG8X and conductor equivalent to Antenex – CN8X from Radio to Antenna and shall be of appropriate length and not longer than 8 ft.

Installation.  I/O Module.  All motherboard cards shall be configured and installed as per manufacturer’s specifications and IDOT specification Ltg SCADA 397.  Modules include but are not limited to; CPU, Mixed I/O.  All digital inputs terminated on the Mixed I/O card shall be dry.  Termination points for all digital input points will be reflected on power center wiring diagram or additional wiring schematic provided by the engineer.  All digital outputs received from the Mixed I/O card shall be rated at 24 VAC 2A.  All digital outputs shall be connected to interposing relays prior to being integrated into the power center wiring logic.  The digital outputs shall maintain a momentary closure for approximately 2 seconds.

All wiring termination points shall be tagged using the nomenclature given on the wiring diagram. The alarms acknowledge button shall be implemented with a placard stating “Alarm Acknowledge”. Site configuration, map implementation, screens tagging and other related software configurations shall be specified elsewhere herein.

The antenna shall be centered on the top of the control cabinet.  The antenna cable shall be dressed and trimmed for minimal length, allowing sufficient slack of removal of the radio connection for replacement or testing without disruption to the installation.  The antenna connector shall be properly soldered to the cable assembly. Great care shall be exercised in the assembly of the antenna connector, excessive heat will destroy the inner insulation, and insufficient heat will produce a cold solder connection on the outer shield.

Intra-module wiring shall be 18 AWG stranded wire, color coded (American) consistent with battery polarity, and signal.  The wire connection from terminal block (TB2) to the interpose relays shall be 14AWG stranded.  All wires connected to the radio modules shall be dressed and tinned prior to insertion, (crimp on connectors will not be allowed for use in the radio system).  Cost of all wire is inclusive within the scope of this work.

A terminal strip separate from the integral radio module and power supply shall be provided to interface power and signal conductors to the lighting controller.  Terminals and wiring shall be labeled in accordance with the drawings, and dressed to allow service.  The radio module shall be provided with constant 240 VAC power.  The control power breaker shall provide power for the SCADA system.  This is to allow the system to be energized at all times.

The SCADA system shall be tested in conjunction with the controller inspection, prior to field installation.  The turn-on and turn-off function shall be tested ten (10) consecutive times utilizing actual signals originating from District 1 Headquarters.  Any failures must be cleared before the controller is delivered to the job site.

Null covers shall be provided for the slots not used.  All analog inputs shall be 4-20 mA.  All I-O wiring including analog and digital shall be wired as per the enclosed table.

SCADA System Control Relay Assembly.  The Contractor shall mount and wire four (4) relays in a box as shown in the wiring diagram.  Two relays shall be 240 volts sealed type and two relays shall be 24 volts sealed type, unless otherwise indicated, shall have contacts rated at not less than 20 amperes at 240 volts.  The power relay for activating the lighting contactors shall have contacts rated to handle the contactor inrush.  The relays shall be wired to a marked terminal strip.

Testing.  As part of final acceptance testing, all individual I/O points and internal status alarms shall be tested for proper operation and transmission. The transmission shall be confirmed at IDOT District 1 HQ. and the contractors dispatch facility.  This full SCADA system start-up shall be completed with the Engineer present.

The SCADA radio system shall have the following items tested: VSWR, cable impedance, RSSI to the power center and confirmation that data sent from power center is received by the IDOT lighting system computers.

Analog Inputs And Transducers.  The panel shall include one voltage transducer for monitoring the line voltage and one current transducer for monitoring the neutral current.  Their outputs shall be 4-20 mA DC each and shall be wired to channels 1 and 2 of the Mixed I/O module as shown.  The voltage transducer shall be Scientific Columbus Model # VT110 – PAN7 – A4-2 for 480/240 volt single phase systems.  The current transducers shall be Mel Kirchler Technologies Model # AT2-420-24L-FT, with power supply, PS-240-24P-1A.  Both analog inputs shall be wired using shielded cable.  Both transducers shall also be calibrated so that the SCADA system reads the correct value.

Testing Of The Assembled Cabinet.  Prior to shipment of the completed control cabinet, the control cabinet shall be tested for load, short circuits and complete operation of the cabinet as specified herein and as shown on the plans. The test shall be made at the manufacturer’s shop, by the manufacturer and shall be witnessed by the Engineer. The Contractor shall arrange the test date with the Engineer and so allow not less than seven (7) days advance notice. The cabinet shall not be delivered to the job site until inspected, tested and approved for delivery by the Engineer.

Staging.  All Central Configuration programming be completed prior to the initial check out/PM of the SCADA unit in the field. This is to assure/confirm 2 way radio communications from the field RTU the Central. Lighting controller information submitted for approval shall include any recommendations of the Manufacturer for storage as provided under this contract.

The packaging of the lighting controller shall incorporate the provisions recommended by the Manufacturer to accommodate storage.

| TERM | MOSCAD DESTINATION | WIRE # | DESCRIPTION OF INPUT |
| --- | --- | --- | --- |
| 32 | Analog Input 1 (+) | TB2 B11 | CABINET NEUTRAL CURRENT |
| 33 | Analog Input 1 (-) | TB2 B1 | CABINET NEUTRAL CURRENT |
| 34 | Analog Input 2 (+) | TB2 A2 | CABINET SERVICE VOLTAGE |
| 35 | Analog Input 2 (-) | TB2 B2 | CABINET SERVICE VOLTAGE |
| 40 | P. Ground | TB2 A3 | GROUND |
| 1 | Digital Input 1 | TB2 B3 | ALARM ACKNOWLEDGE |
| 2 | Digital Input 2 | TB2 A4 | DOOR OPEN |
| 3 | Digital input 3 | TB2 A5 | MAIN(S) BREAKER OPEN |
| 4 | Digital input 4 | TB2 A7 | CONTACTOR 1 OPEN |
| 5 | Digital Input 5 | TB2 A8 | CONTACTOR 2 OPEN |
| 6 | Digital input 6 | TB2 A9 | CABINET IN NON-AUTO |
| 7 | Digital input 7 | TB2 A10 | BACK-UP CLOCK OFF CALL |
| 8 | Digital Input 8 | TB2 A11 | BACK-UP CLOCK ON CALL |
| 18 | DI Common | * | COMMON |
| 20 | K1 NO | TB2 A12 | LIGHTS ON CALL |
| 21 | K1 Com | TB2 B17 | K1 COMMON |
| 23 | K2 NO | TB2 A13 | LIGHTS OFF CALL |
| 24 | K2 Com | TB2 B17 | K2 COMMON |
| 17 | 24 V+ | TB2 B13 | 24+ VDC |

All analog inputs will be 4-20 mA only. Digital output relays will be electrically energized and momentarily held.

Mixed I/O module model number V 245

Lighting SCADA RTU terminal Configuration.

Description.  This work shall consist of having the SCADA system manufacturer design, implement and test a new RTU on the Lighting SCADA System on all system terminals.

Materials.  All software work shall be completed by the manufacturer or approved factory licensed sales and service company for the SCADA equipment. All licensing shall be provided by the entity completing the work. Licenses are to be held by IDOT.

SCADA RTU Configuration And Programming:

- Setup of CPU and accompanying modules.

- Setup of RTU site number, octal address, group call and All Call.

- Configure application alarm parameters (download config./application).

- Development and implementation of control and alarm application from IDOT submitted telemetry requirements.

NOTE:  IDOT shall supply checklist listing I/O, telemetry, all call, group call and individual call data.

SCADA Service/Client Wonderware Programming:

- Add RTU to Wonderware.

- Configure Wonderware to poll SCADA CPU for data on that specific RTU.

- Setup servers and clients for alarm notification and database I/O, for that specific RTU.

- Configure RTU polling.

- Activate RTU on FIU polling.

SCADA FIU CPU Programming:

If RTU exists as an Intrac site, it will have to be setup as a MOSCAD site (MOSCAD CPU).  If RTU is a new site, it will have to be configured as a MOSCAD site (MOSCAD CPU).

Submittals.  The Motorola VAR shall submit ladder programming, quiescent telemetry and SCADA configuration files for approval by the IDOT Engineer. Submittal will be reviewed by the Engineer and returned noting changes and/or comments.

Testing and Documentation.  As part of final acceptance testing, all individual I/O points and internal status (COS) alarms shall be tested for proper operation and transmission.  The transmission shall be confirmed at IDOT Dist. HQ. And the contractors dispatch facility.  This full SCADA system start-up shall be completed with the Engineer present.

The control cabinet shall be tested for complete operation and the electrical load on each circuit shall be measured and documented on the Log form L-3. The ground resistance test shall be performed by the Contractor using the fall-of-potential method, with results recorded by the Contractor and witnessed by the Engineer.  Ground continuity shall be tested using an approved low-impedance ohmmeter, to the farthest point of each circuit extension from the controller cabinet.  Results shall be recorded by the Contractor and witnessed by the Engineer.

Installation.

The lighting controller installation shall be according to the details, location, and orientation shown on the plans.

Work Pad.  A 4 in. (100 mm) thick portland cement concrete work pad, not less than 48 x 48 in. (1.2 x 1.2 m) shall be provided in front of the cabinet, except where the cabinet faces an adjacent sidewalk.

All conduit entrances into the lighting controller shall be sealed with a pliable waterproof material.

Concrete Foundation.  The Contractor shall confirm the orientation of the lighting controller, and its door side, with the Engineer, prior to installing the foundation.  A portland cement concrete foundation shall be constructed to the details shown on the plans and is included as a part of this pay items and shall not be paid for separately.  The top of the foundation shall be 12-inches above grade.

The lighting controller enclosure shall be set plumb and level on the foundation. It shall be fastened to the anchor rods with hot-dipped galvanized or stainless steel nuts and washers.  Foundation mounted lighting controllers shall be caulked at the base with silicone.

Where the controller has a metal bottom plate, the plate shall be sealed with a rodent and dust/moisture barrier.

Grounding.

Grounding shall be as shown on the lighting controller detail drawings.  Ground rods, ground wells, connections, ground wire and other associated items shall be included in the cost the lighting controller and shall not be paid for separately.”

Method Of Measurement.  Each lighting controller shall be counted each for payment.

Basis Of Payment.  This item shall be paid for at the contract unit price each for LIGHTING CONTROLLER, BASE MOUNTED, 480 VOLT, 200 AMP (DUAL), RADIO SCADA, which shall be payment in full for the work, complete, as specified herein.