## Tracer Wire

Effective:  December 1, 2024

Description.  This work shall consist of furnishing and installing tracer wire in raceways, complete with all splicing, identifications, and terminations.  A tracer wire shall be installed with all fiberoptic raceways such as innerduct, metallic raceways or nonmetallic raceways installed underground, under the pavement, in trench or in conduit embedded in structures or attached to structures.  Only one tracer wire per each raceway is required.  If there are parallel raceways, a tracer wire is required for each raceway. Tracer wire shall be installed in raceway segments to provide a continuous tracer wire system. Multi-cell fiber optic micro duct with an integral tracer wire does not require a separate external tracer wire unless required by the contract.

Materials.  The tracer wire shall be a direct burial rated, number 12 AWG (minimum) solid (.0808” diameter), fully annealed, high carbon steel, extra high strength solid copper-clad steel tracer wire. The wire shall have a minimum break load of 1150 lbs.  The wire shall have a 45 mil high density orange polyethylene (HDPE) jacket complying with ASTM-D-1248, rated for direct burial use at 600 volts.

Wire must conform to ASTM B1010. Copper is UNS-C10200, OF Copper in accordance with ASTM B-170. The conductor must be meet or exceed 21% conductivity.

Connection devices used shall be as approved by the tracer wire manufacturer, except wire nuts of any type are not acceptable and shall not be used.

Installation.  Tracer wire shall be installed without damaging the insulation.  The tracer wire shall be installed in the same trench as the fiberoptic raceway. When the fiber optic raceway is installed in conduit under pavement or in conduit embedded in structures or attached to structures, the tracer wire shall be installed in the same conduit as the fiber optic raceway.

Tracer wire cable extended to camera poles, ITS poles, ITS cabinets and similar equipment shall be of length sufficient for cable splices to be withdrawn a minimum of 18 inches out of pole handholes or similar equipment.  Tracer wire shall follow all bending radius and pulling tensions of manufacturer.

The tracer cable shall be installed directly from the reels on which the cable was shipped.  The cable shall be installed in continuous spans between terminal points and splicing will only be permitted in pole handholes, junction boxes, handholes, vaults, and communication huts and similar locations.

Tracer wires shall be tagged inside locate posts or access points. The tag shall show the fiber owner, fiber count, fiber type, direction, distance to next locate post and mile post at that location

Testing.  Tracer wire shall be tested for continuity and locate-ability prior to the installation of any fiber optic cable.

Method of Measurement.  The tracer wire will be measured for payment in feet in place.  Measurements will be made in straight lines between changes in direction and to the center of equipment, handholes, vaults, or junction boxes.

Bais of Payment.   This work will be paid for at the contract unit price per foot installed for TRACER WIRE, of the size specified.