# UNDERPASS LUMINAIRE, LED

Effective:  November 1, 2025

Description.

This work shall consist of furnishing and installing an underpass LED luminaire as shown on the plans, as specified herein.

General.

The luminaire including the housing, driver and optical assembly shall be assembled in the U.S.A. The luminaire shall be assembled by and manufactured by the same manufacturer. The luminaire shall be mechanically strong and easy to maintain. All electrical and electronic components of the luminaire shall comply with the requirements of Restriction of Hazardous Materials (RoHS) regulations. The luminaire shall be listed for wet locations by an NRTL and shall meet the requirements of UL 1598 and UL 8750

Submittal Requirements.

The Contractor shall also the following manufacturer's product data for each type of luminaire:

- Descriptive literature and catalogue cuts for luminaire, LED driver, and surge protection device. Completed manufacturer’s luminaire ordering form with the full catalog number provided

- LED drive current, total luminaire input wattage and total luminaire current at the system operating voltage or voltage range and ambient temperature of 25 C.

- LED efficacy per luminaire expressed in lumens per watt (l/w).

- Initial delivered lumens at the specified color temperature, drive current, and ambient temperature.

- IES file associated with each submitted luminaire in the IES LM-63 format.

- Computer photometric calculation reports as specified and in the luminaire performance table.

- TM-15 BUG rating report.

- lsofootcandle chart with max candela point and half candela trace indicated.

- Documentation of manufacturers experience and verification that luminaires were assembled in the U.S.A. as specified.

- Written warranty.

Upon request by the Engineer, submittals shall also include any or all the following:

- TM-21 calculator spreadsheet (XLSX or PDF format) and if available, TM-28 report for the specified luminaire or luminaire family. Both reports shall be for 50,000 hours at an ambient temperature of 77 °F (25 °C).

- LM-79 report with National Voluntary Laboratory Accreditation Program (NVLAP) current at the time of testing in PDF format inclusive of the following: isofootcandle diagram with half candela contour and maximum candela point; polar plots through maximum plane and maximum cone; coefficient of utilization graph; candela table; and spectral distribution graph and chromaticity diagram.

- LM-80 report for the specified LED package in PDF format and if available, LM-84 report for the specified luminaire or luminaire family in PDF format. Both reports shall be conducted by a laboratory with NVLAP certification current at the time of testing.

- AGi32 calculation file matching the submittal package.

- In Situ Temperature Measurement Test (ISTMT) report for the specified luminaire or luminaire family in PDF format.

- Vibration test report in accordance with ANSI C136.31 in PDF format.

- ASTM B117/ASTM D1654 (neutral salt spray) test and sample evaluation report in PDF format.

- ASTM G154 (ASTM D523) gloss test report in PDF format.

- LED drive current, total luminaire input wattage, and current over the operating voltage range at an ambient temperature of 77 °F (25 °C).

- Power factor (pf) and total harmonic distortion (THD) at maximum and minimum supply and at nominal voltage for the dimmed states of 70%, 50%, and 30% full power.

- Ingress protection (IP) test reports, conducted according to ANSI C136.25 requirements, for the driver and optical assembly in PDF format.

- Installation, maintenance, and cleaning instructions in PDF format, including recommendations on periodic cleaning methods.

- Documentation in PDF format that the reporting laboratory is certified to perform the required tests.

A sample luminaire shall also be provided upon request of the Engineer.  The sample shall be as proposed for the contract and shall be delivered by the Contractor to the District Headquarters.  After review, the Contractor shall retrieve the luminaire.

Manufacturer Experience.

The luminaire shall be designed to be incorporated into a lighting system with an expected 20 year lifetime. The luminaire manufacturer shall have a minimum of 15 years’ experience manufacturing LED roadway luminaires; parking lot, architectural, or residential luminaires are not applicable to this requirement. The manufacturer shall have a minimum of 100,000 total LED roadway luminaires installed on a minimum of 100 separate installations, all within the U.S.A.

Housing.

Material. The luminaire shall be a single device not requiring on­site assembly for installation.  The power supply for the luminaire shall be integral to the unit.  The housing shall be either stainless-steel or cast aluminum.

Aluminum Housing.

The housing shall be extruded or cast aluminum; or a combination of both and shall have a copper content of less than 1.0%.

The housing shall be painted grey or silver unless specified otherwise.  A epoxy base coat shall applied to the aluminum after the aluminum is properly treated with a conversion coating.  The finish coat shall be polyester powder coat with a minimum thickness of 2.0 mil.

The luminaire surfaces exposed to the environment shall exceed a rating of six, according to ASTM D1654, after 1000 hours of ASTM B117 testing. The coating shall exhibit no greater than 30% reduction of gloss, according to ASTM D523, after 500 hours of ASTM G154 Cycle 6 QUV® accelerated weathering testing.

Stainless-Steel Housing.

The housing shall be constructed from 16-gauge minimum, 304 stainless steel.

The stainless-steel housing does not need to be painted.  The manufacturer may paint the luminaire at no additional cost.

The luminaire shall be optically sealed, mechanically strong and easy to maintain.  The luminaire shall be designed for wall mounting to a pier or abutment.  It shall be provided with a suitable mounting bracket which allows for +90° adjustment from horizontal in 5° increments.

The luminaire shall be gasketed and sealed and shall be UL listed for wet locations.  The luminaire optical assembly shall have a minimum IEC ingress penetration rating of IP66.  When furnished with a lens and frame, the lens shall be made of crystal clear, impact and heat resistant flat glass. The lens and frame shall be securely attached to the main housing and be readily removable for servicing the LED optical assembly.

All external surfaces shall be cleaned in accordance with the manufacturer’s recommendations and be constructed in such a way as to discourage the accumulation of water, ice, and debris.

The total weight including accessories, shall not exceed 75 lbs.

A passive cooling method with no moving, rotating parts, or liquids shall be employed for heat management.

Vibration Testing. All luminaires shall be subjected to and pass vibration testing requirements at “3G” minimum zero to peak acceleration in accordance with ANSI C136.31 requirements using the same luminaire. To be accepted, the luminaire housing, hardware, and each individual component shall pass this test with no noticeable damage and the luminaire must remain fully operational after testing.

Labels.  An internal label shall be provided indicating the luminaire is suitable for wet locations and indicating the luminaire is an NRTL listed product to UL1598 and UL8750. The internal label shall also comply with the requirements of ANSI C136.22.

An external label consisting of two black characters on a white background with the dimensions of the label and the characters as specified in ANSI C136.15 for HPS luminaires. The first character shall be the alphabetical character representing the initial lumen output as specified in Table 1 of Article 1067.06(c). The second character shall be the numerical character representing the transverse light distribution type as specified in IES RP-8 (i.e. Types 1, 2, 3, 4, or 5).

Hardware. All hardware shall be stainless steel or of other corrosion resistant material approved by the Engineer.

Luminaires shall be designed to be easily serviced, having fasteners such as quarter-turn clips of the heavy spring-loaded type with large, deep straight slot heads, complete with a receptacle and shall be according to military specification MIL-f-5591.

All hardware shall be captive and not susceptible to falling from the luminaire during maintenance operations. This shall include lens/lens frame fasteners as well hardware holding the removable driver and electronic components in place.

Circuiting shall be designed to minimize the impact of individual LED failures on the operation of the other LED’s.

Wiring.  Wiring within the electrical enclosure shall be rated at 600v, 105°C or higher.

The power connection to the luminaire shall be via liquid tight metallic conduit or an armored flexible cable assembly.  The power connection, including any external shielding, must be secured to the luminaire and connected source. The location of the opening shall be coordinated with the installation to minimize the length of flexible conduit required. The length of the cable or flexible conduit shall not exceed six (6) feet.

Mounting Brackets.

The brackets shall be properly sized to accommodate the weight of the luminaire with calculations or other suitable reference documentation submitted to support the material choice.  The brackets shall be constructed of 304 stainless steel

The mounting brackets shall be fully coordinated with the luminaire mounting method indicated in plans.

Driver.

The driver shall be integral to the luminaire shall be capable of receiving an indefinite open and short circuit output conditions without damage.

The driver shall incorporate the use of thermal foldback circuitry to reduce output current under abnormal driver case temperature conditions and shall be rated for a lifetime of 100,000 hours at an ambient temperature exposure of 77 °F (25 °C) to the luminaire. If the driver has a thermal shut down feature, it shall not turn off the LEDs when operated at 104 °F (40 °C) or less.

The driver shall have an input voltage range of 120 to 277 volts (± 10%) or 347 to 480 volts (± 10%) according to the contract documents. When the driver is operating within the rated input voltage range and in an un-dimmed state, the power factor measurement shall be not less than 0.9 and the THD measurement shall be no greater than 20%.

The driver shall meet the requirements of the FCC Rules and Regulations, Title 47, Part 15 for Class A devices with regard to electromagnetic compatibility. This shall be confirmed through the testing methods in accordance with ANSI C63.4 for electromagnetic interference.

The driver shall be dimmable using the protocol listed in the Luminaire Performance Table shown in the contract.

Surge Protection.   The luminaire shall comply the requirements of ANSI C136.2 for electrical transient immunity at the “Extreme” level (20KV/10KA) and shall be equipped with a surge protective device (SPD) that is UL1449 compliant. An SPD failure shall open the circuit to protect the driver.

LED Optical Assembly

The optical assembly shall have an IP66 or higher rating in accordance with ANSI C136.25. The circuiting of the LED array shall be designed to minimize the effect of individual LED failures on the operation of other LEDs. All optical components shall be made of glass or a UV stabilized, non-yellowing material.

The optical assembly shall utilize high brightness, long life, minimum 70 CRI, 4,000K color temperature (+/-300K) LEDs binned in accordance with ANSI C78.377. Lenses shall be UV-stabilized acrylic or glass.

The actual measured luminous flux output shall be within +/- 10% of the published lumen value.

Lumen depreciation at 50,000 hours of operation shall not exceed 15% of initial lumen output at the specified LED drive current and an ambient temperature of 25° C.

The luminaire may or may not have a glass lens over the LED modules. If a glass lens is used, it must be a flat lens.  Material other than glass will not be acceptable. If a glass lens is not used, the LED modules may not protrude lower than the luminaire housing.

The assembly shall have individual serial numbers or other means for manufacturer tracking.

Photometric Performance.

Luminaires shall be tested according to IESNA LM-79. This testing shall be performed by a test laboratory holding accreditation from the National Institute of Standards and Technology (NIST) National Voluntary Laboratory Accreditation Program (NVLAP) for the IESNA LM-79 test procedure.

Data reports as a minimum shall yield an isofootcandle chart, with max candela point and half candela trace indicated, maximum plane and maximum cone plots of candela, a candlepower table (house and street side), a coefficient of utilization chart, a luminous flux distribution table, spectral distribution plots, chromaticity plots, and other standard report outputs of the above-mentioned tests.

The luminaire shall have a BUG rating of Back Light B3 or less, Up Light rating of U0, and a Glare rating of G3 or less unless otherwise indicated in the luminaire performance table.

Photometric Calculations.

Calculations. Submitted report shall include a luminaire classification system graph with both the recorded lumen value and percent lumens by zone along with the BUG rating according to IESNA TM-15.

Complete point-by-point luminance and veiling luminance calculations as well as listings of all indicated averages and ratios as applicable shall be provided in accordance with IESNA RP-8 recommendations. Lighting calculations shall be performed using AGi32 software with all luminance calculations performed to one decimal place (i.e. x.x cd/m2). Uniformity ratios shall also be calculated to one decimal place (i.e. x.x:1).  Calculation results shall demonstrate that the submitted luminaire meets the lighting metrics specified in the project Luminaire Performance Table(s).  Values shall be rounded to the number of significant digits indicated in the luminaire performance table(s).

When the quantity of luminaires requires independent testing, the AGi32 calculation file used for performance verification shall also be submitted with the initial submittal.

All photometry must be photopic. Scotopic or mesopic factors will not be allowed. The AGi32 file shall be submitted at the request of the Engineer.

The luminaire may have an initial lumen value lower that the specified lumen range in the performance tables provided that the resulting calculations demonstrate that the performance requirements are being met.

| IDOT DISTRICT 1 LUMINAIRE PERFORMANCE TABLE 1 |  |  |  |  |
| --- | --- | --- | --- | --- |
| ROADWAY UNDERPASS LIGHTING 1 LANE |  |  |  |  |
| Given Conditions |  |  |  |  |
| Roadway Data | Pavement Width | 16 |  | (ft) |
|  | Number of Lanes | 1 |  |  |
|  | I.E.S. Surface Classification | R3 |  |  |
|  | Q-Zero Value | .07 |  |  |
| Mounting Data | Mounting Height | 15 |  | (ft) |
|  | Tilt | 0-30 |  | (degrees) |
|  | Orientation | Perpendicular to roadway |  |  |
|  | Set-Back from Edge Of Pavement | 12 |  | (ft) |
| Luminaire Data | Lumens | 10,000 – 13,500 |  |  |
|  | Total Light Loss Factor | 0.65 |  |  |
| Layout Data | Spacing | 40 |  | (ft) |
|  | Configuration | Single Sided |  |  |
|  | Luminaire Overhang over EOP | -12 |  | (ft) |
| NOTE: Variations from the above specified I.E.S. distribution pattern may be requested and acceptance of variations will be subject to review by the Engineer based on how well the performance requirements are met. |  |  |  |  |
| Performance Requirements |  |  |  |  |
| NOTE: These performance requirements shall be the minimum acceptable standards of photometric performance for the luminaire, based on the given conditions listed above. |  |  |  |  |
| Roadway | Average Luminance, LAVE | 1.6 | Cd/m2 (Max) |  |
|  |  | 1.2 | Cd/m2 (Min) |  |
| Luminance | Uniformity Ratio, LAVE/LMIN | 3:1 | (Max) |  |
|  | Uniformity Ratio, LMAX/LMIN | 5:1 | (Max) |  |
|  | Veiling Luminance Ratio, LV/LAVE | 0.30:1 | (Max) |  |

| IDOT DISTRICT 1 LUMINAIRE PERFORMANCE TABLE 2 |  |  |  |  |
| --- | --- | --- | --- | --- |
| ROADWAY UNDERPASS LIGHTING 2 LANE |  |  |  |  |
| Given Conditions |  |  |  |  |
| Roadway Data | Pavement Width | 24 |  | (ft) |
|  | Number of Lanes | 2 |  |  |
|  | I.E.S. Surface Classification | R3 |  |  |
|  | Q-Zero Value | .07 |  |  |
| Mounting Data | Mounting Height | 15 |  | (ft) |
|  | Tilt | 0-30 |  | (degrees) |
|  | Orientation | Perpendicular to roadway |  |  |
|  | Set-Back from Edge Of Pavement | 12 |  | (ft) |
| Luminaire Data | Lumens | 10,000 – 13,500 |  |  |
|  | Total Light Loss Factor | 0.65 |  |  |
| Layout Data | Spacing | 35 |  | (ft) |
|  | Configuration | Single Sided |  |  |
|  | Luminaire Overhang over EOP | -12 |  | (ft) |
| NOTE: Variations from the above specified I.E.S. distribution pattern may be requested and acceptance of variations will be subject to review by the Engineer based on how well the performance requirements are met. |  |  |  |  |
| Performance Requirements |  |  |  |  |
| NOTE: These performance requirements shall be the minimum acceptable standards of photometric performance for the luminaire, based on the given conditions listed above. |  |  |  |  |
| Roadway | Average Luminance, LAVE | 1.6 | Cd/m2 (Max) |  |
|  |  | 1.2 | Cd/m2 (Min) |  |
| Luminance | Uniformity Ratio, LAVE/LMIN | 3:1 | (Max) |  |
|  | Uniformity Ratio, LMAX/LMIN | 5:1 | (Max) |  |
|  | Veiling Luminance Ratio, LV/LAVE | 0.30:1 | (Max) |  |

| IDOT DISTRICT 1 LUMINAIRE PERFORMANCE TABLE 3 |  |  |  |  |
| --- | --- | --- | --- | --- |
| ROADWAY UNDERPASS LIGHTING 3 LANE |  |  |  |  |
| Given Conditions |  |  |  |  |
| Roadway Data | Pavement Width | 36 |  | (ft) |
|  | Number of Lanes | 3 |  |  |
|  | I.E.S. Surface Classification | R3 |  |  |
|  | Q-Zero Value | .07 |  |  |
| Mounting Data | Mounting Height | 15 |  | (ft) |
|  | Tilt | 0-30 |  | (degrees) |
|  | Orientation | Perpendicular to roadway |  |  |
|  | Set-Back from Edge Of Pavement | 12 |  | (ft) |
| Luminaire Data | Lumens | 10,000 – 13,500 |  |  |
|  | Total Light Loss Factor | 0.65 |  |  |
| Layout Data | Spacing | 50 |  | (ft) |
|  | Configuration | Opposite |  |  |
|  | Luminaire Overhang over EOP | -12 |  | (ft) |
| NOTE: Variations from the above specified I.E.S. distribution pattern may be requested and acceptance of variations will be subject to review by the Engineer based on how well the performance requirements are met. |  |  |  |  |
| Performance Requirements |  |  |  |  |
| NOTE: These performance requirements shall be the minimum acceptable standards of photometric performance for the luminaire, based on the given conditions listed above. |  |  |  |  |
| Roadway | Average Luminance, LAVE | 1.6 | Cd/m2 (Max) |  |
|  |  | 1.2 | Cd/m2 (Min) |  |
| Luminance | Uniformity Ratio, LAVE/LMIN | 3:1 | (Max) |  |
|  | Uniformity Ratio, LMAX/LMIN | 5:1 | (Max) |  |
|  | Veiling Luminance Ratio, LV/LAVE | 0.30:1 | (Max) |  |

| IDOT DISTRICT 1 LUMINAIRE PERFORMANCE TABLE 4 |  |  |  |  |
| --- | --- | --- | --- | --- |
| ROADWAY UNDERPASS LIGHTING 4 LANE |  |  |  |  |
| Given Conditions |  |  |  |  |
| Roadway Data | Pavement Width | 48 |  | (ft) |
|  | Number of Lanes | 4 |  |  |
|  | I.E.S. Surface Classification | R3 |  |  |
|  | Q-Zero Value | .07 |  |  |
| Mounting Data | Mounting Height | 15 |  | (ft) |
|  | Tilt | 0-15 |  | (degrees) |
|  | Orientation | Perpendicular to roadway |  |  |
|  | Set-Back from Edge Of Pavement | 12 |  | (ft) |
| Luminaire Data | Lumens | 10,000 – 13,500 |  |  |
|  | Total Light Loss Factor | 0.65 |  |  |
| Layout Data | Spacing | 45 |  | (ft) |
|  | Configuration | Opposite |  |  |
|  | Luminaire Overhang over EOP | -12 |  | (ft) |
| NOTE: Variations from the above specified I.E.S. distribution pattern may be requested and acceptance of variations will be subject to review by the Engineer based on how well the performance requirements are met. |  |  |  |  |
| Performance Requirements |  |  |  |  |
| NOTE: These performance requirements shall be the minimum acceptable standards of photometric performance for the luminaire, based on the given conditions listed above. |  |  |  |  |
| Roadway | Average Luminance, LAVE | 1.6 | Cd/m2 (Max) |  |
|  |  | 1.2 | Cd/m2 (Min) |  |
| Luminance | Uniformity Ratio, LAVE/LMIN | 3:1 | (Max) |  |
|  | Uniformity Ratio, LMAX/LMIN | 5:1 | (Max) |  |
|  | Veiling Luminance Ratio, LV/LAVE | 0.30:1 | (Max) |  |

| IDOT DISTRICT 1 LUMINAIRE PERFORMANCE TABLE 5 |  |  |  |  |
| --- | --- | --- | --- | --- |
| ROADWAY UNDERPASS LIGHTING 5 LANE |  |  |  |  |
| Given Conditions |  |  |  |  |
| Roadway Data | Pavement Width | 60 |  | (ft) |
|  | Number of Lanes | 5 |  |  |
|  | I.E.S. Surface Classification | R3 |  |  |
|  | Q-Zero Value | .07 |  |  |
| Mounting Data | Mounting Height | 15 |  | (ft) |
|  | Tilt | 0-15 |  | (degrees) |
|  | Orientation | Perpendicular to roadway |  |  |
|  | Set-Back from Edge Of Pavement | 12 |  | (ft) |
| Luminaire Data | Lumens | 10,000 – 13,500 |  |  |
|  | Total Light Loss Factor | 0.65 |  |  |
| Layout Data | Spacing | 40 |  | (ft) |
|  | Configuration | Opposite |  |  |
|  | Luminaire Overhang over EOP | -12 |  | (ft) |
| NOTE: Variations from the above specified I.E.S. distribution pattern may be requested and acceptance of variations will be subject to review by the Engineer based on how well the performance requirements are met. |  |  |  |  |
| Performance Requirements |  |  |  |  |
| NOTE: These performance requirements shall be the minimum acceptable standards of photometric performance for the luminaire, based on the given conditions listed above. |  |  |  |  |
| Roadway | Average Luminance, LAVE | 1.6 | Cd/m2 (Max) |  |
|  |  | 1.2 | Cd/m2 (Min) |  |
| Luminance | Uniformity Ratio, LAVE/LMIN | 3:1 | (Max) |  |
|  | Uniformity Ratio, LMAX/LMIN | 5:1 | (Max) |  |
|  | Veiling Luminance Ratio, LV/LAVE | 0.30:1 | (Max) |  |

Wall Mounted Underpass Luminaire

Suspened Underpass Luminaire

Independent Testing

When a contract has 30 or more luminaires of the same type (distribution type and lumen output/wattage), that luminaire type shall be independently tested, unless otherwise noted. The quantity of luminaires to be tested shall be as specified in the following table.

| Contract Quantity | Luminaires to be Tested |
| --- | --- |
| 1-49 | 0 (unless otherwise noted) |
| 50-100 | 2 |
| 101-150 | 3 |
| 151-200 | 4 |
| 201-250 | 5 |
| 251-300 | 6 |
| 301-350 | 7 |

Testing is not required for temporary lighting luminaires.

The Contractor shall coordinate the testing with the contract schedule considering submittal, manufacturing, testing, and installation lead-times and deadlines.

The Electrical Engineer shall select from all the project luminaires at the Contractor's or distributor’s storage facility, within District 1, the luminaires for testing. In all cases, the selection of luminaires shall be a random selection from the entire completed lot of luminaires required for the contract. Selections from partial lots will not be allowed.  An additional luminaire shall also be selected for physical inspection by the Engineer at the District Headquarters.  This luminaire will be available for the Contractor to pick up at a later date to be installed under this contract.  This luminaire is in addition to the luminaire required as a part of the submittal process specified elsewhere.

Alternative selection process.  With the Engineer’s prior approval, the Contractor shall provide a list of luminaire serial numbers for all the luminaires.  The Engineer shall make a random selection of the required number of luminaires for testing from the serial numbers.  That luminaire must then be photographed clearly showing the serial number prior to shipment to the selected and approved testing laboratory.  The testing laboratory shall include a photograph of the luminaire along with the test results directly to the Engineer.

Luminaires shall be tested at a National Voluntary Laboratory Accreditation Program (NVLAP) accredited laboratory approved for each of the required tests.  The testing facility shall not be associated in any way, subsidiary or otherwise, with the luminaire manufacturer.  All costs associated with luminaire testing shall be included in the bid price of the luminaire.

The selection of the proposed independent laboratory shall be presented with the information submitted for review and approval.

The testing performed shall include photometric and electrical testing.

All tests shall be conducted at the luminaire system operating voltage of 240 volts unless specified differently in the contract plans.

Photometric testing shall be according to IES recommendations, performed with a goniophotometer and as a minimum, shall yield an isofootcandle chart, with max candela point and half candela trace indicated, an isocandela diagram, maximum planned and maximum cone plots of candela, a candlepower table (House and street side), a coefficient of utilization chart, a luminous flux distribution table, BUG rating report, and complete calculations based on specified requirements and test results.

Electrical testing shall conform to NEMA and ANSI standards and, as a minimum shall include a complete check of wiring connections and a table of characteristics showing input amperes, watts, power factor, total harmonic distortion and LED drive current.

The summary report and the test results including IES photometric files shall be sent directly to the Resident Engineer, the Electrical Engineer, and the Contractor via email or other mutually agreeable means.

Photometric performance shall meet or exceed that of the specified values. The color temperature shall be within +/- 300°K of the submitted factory values. The measured lumen output of the luminaire shall be within +/- 10% of the submitted factory value. If the luminaire does not meet the specified photometric values, the luminaire has failed regardless of whether the test results meet the submitted factory data.

Should any of the tested luminaires of a given type, and distribution fail to satisfy the specifications and perform according to approved submittal information, the luminaire type of that distribution type and wattage shall be unacceptable and be replaced by alternate equipment meeting the specifications with the submittal and testing process repeated in their entirety; or corrections made to achieve required performance.

In the case of corrections, the Contractor shall advise the Engineer of the proposed corrections and shall request a repeat of the specified testing and, if the corrections are deemed reasonable by the Engineer, the testing process shall be repeated in its entirety.

The number of luminaires to be tested shall be the same quantity as originally tested as required in the above table.

Retesting, should it become necessary, shall not be grounds for additional compensation or extension of time.

Submittal information shall include a statement of intent to provide the testing as well as a request for approval of the chosen laboratory.

Installation.

Each luminaire shall be installed according to the luminaire manufacturer’s recommendations.

Underpass luminaires shall be either attached to structures (such as piers, etc.) or suspended from structures (such as bridge decks) as indicated or implied by the configuration on the Plans.  Mounting, including all hardware and appurtenant items, shall be included as part of this item. Luminaires shall be configured with the luminaire tilt as identified in the submitted documents.

Unless otherwise indicated, suspended underpass luminaires shall be installed one-inch above the lowest underpass beam and shall be mounted using vibration dampening assemblies.  All mounting hardware shall be corrosion resistant and shall be stainless steel unless otherwise indicated.

No luminaire shall be installed prior to approval. Where independent testing is required, full approval will not be given until complete test results, demonstrating compliance with the specifications, have been reviewed and accepted by the Engineer.

Luminaire wiring shall be provided with the luminaire.  The wiring shall run from the junction box to the luminaire.

Luminaire wire shall be sized No. 10, rated 600 V, RHW/USE-2, and have copper conductors, stranded in conformance with ASTM B 8. Luminaire wire shall be insulated with cross-linked polyethylene (XLP) insulation. The wire shall include a phase, neutral, and green ground wire.  Wires shall be trained within any raceways so as to avoid abrasion or damage to the insulation.

Included with the luminaire wiring shall be fusing located in the handhole or primary junction box.  Fusing shall be according to Article 1065.01 with the exception that fuses shall be 6 amperes.

Each luminaire and optical assembly shall be free of all dirt, smudges, etc. Should the optical assembly require cleaning, a luminaire manufacturer approved cleaning procedure shall be used.

Warranty.

The entire luminaire shall be covered by a 10-year warranty.   Failure is when one or more of the following occur:

1) Negligible light output from more than 10 percent of the discrete LEDs.

2) Significant moisture that deteriorates performance of the luminaire.

3) Driver that continues to operate at a reduced output due to overheating.

The warranty period shall begin on the date of luminaire delivery.  The Contractor shall verify that the Resident Engineer has noted the delivery date in the daily diary.  Copy of the shipment and delivery documentation shall be submitted.

The replacement luminaire shall be of the same manufacturer, model, and photometric distribution as the original.

Method of Measurement.

The rated initial minimum luminous flux (lumen output) of the light source, as installed in the luminaire, shall be according to the following table for each specified output designation.

| Designation Type | Minimum Initial Luminous Flux | Designation Type | Minimum Initial Luminous Flux |
| --- | --- | --- | --- |
| A | 2,200 | E | 9,450 |
| B | 3,150 | F | 12,500 |
| C | 4,400 | G | 15,500 |
| D | 6,300 | H | 25,200 |

Where delivered lumens is defined as the minimum initial delivered lumens at the specified color temperature. Luminaires with an initial luminous flux less than the values listed in the above table will not be acceptable even if they meet the requirements given in the Luminaire Performance table shown in the contract.

Basis of Payment.

This work will be paid for at the contract unit price per each for LUMINAIRE, LED, UNDERPASS, of the mount type and output designation specified.