## Wire and Cable

Effective: January 1, 2012

Add the following to the first paragraph of Article 1066.02(a):

“The cable shall be rated at a minimum of 90C dry and 75C wet and shall be suitable for installation in wet and dry locations, and shall be resistant to oils and chemicals.”

Revise the Aerial Electric Cable Properties table of Article 1066.03(a)(3) to read:

Aerial Electric Cable Properties

| Phase Conductor |  |  |  | Messenger wire |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Size | Stranding | Average |  |  | Minimum | Stranding |
| AWG |  | Insulation |  |  | Size |  |
|  |  | Thickness |  |  | AWG |  |
|  |  | mm | mils |  |  |  |
| 6 | 7 | 1.1 | (45) |  | 6 | 6/1 |
| 4 | 7 | 1.1 | (45) |  | 4 | 6/1 |
| 2 | 7 | 1.1 | (45) |  | 2 | 6/1 |
| 1/0 | 19 | 1.5 | (60) |  | 1/0 | 6/1 |
| 2/0 | 19 | 1.5 | (60) |  | 2/0 | 6/1 |
| 3/0 | 19 | 1.5 | (60) |  | 3/0 | 6/1 |
| 4/0 | 19 | 1.5 | (60) |  | 4/0 | 6/1 |

Add the following to Article 1066.03(b) of the Standard Specifications:

“Cable sized No. 2 AWG and smaller shall be U.L. listed Type RHH/RHW and may be Type RHH/RHW/USE.  Cable sized larger than No. 2 AWG shall be U.L. listed Type RHH/RHW/USE.”

Revise Article 1066.04 to read:

“Aerial Cable Assembly.  The aerial cable shall be an assembly of insulated aluminum conductors according to Section 1066.02 and 1066.03.  Unless otherwise indicated, the cable assembly shall be composed of three insulated conductors and a steel reinforced bare aluminum conductor (ACSR) to be used as the ground conductor. Unless otherwise indicated, the code word designation of this cable assembly is “Palomino”.  The steel reinforced aluminum conductor shall conform to ASTM B-232.  The cable shall be assembled according to ANSI/ICEA S-76-474.”

Revise the second paragraph of Article 1066.05 to read:

“The tape shall have reinforced metallic detection capabilities consisting of a woven reinforced polyethylene tape with a metallic core or backing.”