# SERVICE INSTALLATION (traffic signals)

Effective: May 22, 2002

Revised: March 1, 2024

805.01TS

Revise Section 805 of the Standard Specifications to read:

Description.

This work shall consist of all materials and labor required to install, modify, or extend the electric service installation.  All installations shall meet the requirements of the “District One Standard Traffic Signal Design Details”.

General.

The electric service installation shall be the electric service disconnecting means and it shall be identified as suitable for use as service equipment.

The electric utility contact information is noted on the plans and represents the current information at the time of Contract preparation.  The Contractor must request in writing for service and/or service modification within ten (10) days of Contract award and must follow-up with the electric utility to assure all necessary documents and payment are received by the utility.  The Contractor shall forward copies of all correspondence between the Contractor and utility company to the Engineer and Area Traffic Signal Maintenance and Operations Engineer.  The service agreement and sketch shall be submitted for signature to the IDOT’s Traffic Operations Programs Engineer.

Materials.

- General.  The completed control panel shall be constructed in accordance with UL Std. 508A, Industrial Control Panel, and carry the UL label.  Wire terminations shall be UL listed.

- Enclosures.

- Pole Mounted Cabinet.  The cabinet shall be UL 50, NEMA Type 4X, unfinished single door design, fabricated from minimum 0.080 in. (2.03 mm) thick Type 5052 H-32 aluminum.  Seams shall be continuous welded and ground smooth. Stainless steel screws and clamps shall secure the cover and assure a watertight seal.  The cover shall be removable by pulling the continuous stainless steel hinge pin.  The cabinet shall have an oil-resistant gasket and a lock kit shall be provided with an internal O-ring in the locking mechanism assuring a watertight and dust-tight seal.  The cabinet shall be sized to adequately house all required components with extra space for arrangement and termination of wiring.  A minimum size of 14 in. (350 mm) high, 9 in. (225 mm) wide and 8 in. (200 mm) in depth is required.  The cabinet shall be channel mounted to a wooden utility pole using assemblies recommended by the Vendor.

- Ground Mounted Cabinet.  The cabinet shall be UL 50, NEMA Type 3R unfinished single door design with back panel.  The cabinet shall be fabricated from Type 5052 H-32 aluminum with the frame and door 0.125 in. (3.175 mm) thick, the top 0.250 in. (6.350 mm) thick and the bottom 0.500-inch (12.70 mm) thick.  Seams shall be continuous welded and ground smooth.  The door and door opening shall be double flanged.  The door shall be approximately 80% of the front surface, with a full length tamperproof stainless steel .075 in. (1.91 mm) thick hinge bolted to the cabinet with stainless steel carriage bolts and nylock nuts.  The locking mechanism shall be slam-latch type with a keyhole cover.  The cabinet shall be sized to adequately house all required components with extra space for arrangement and termination of wiring. A minimum size of 40 in. (1000 mm) high, 16 in. (400 mm) wide and 15 in. (375 mm) in depth is required.  The cabinet shall be mounted upon a Type A concrete foundation as indicated on the plans.  The foundation is paid for separately.

- All enclosures shall include a green external power indicator LED light with circuitry as shown in the Electrical Service-Panel Diagram detail sheet.  For pole mounted service enclosures, the power indicator light shall be mounted as shown in the detail.  For ground mounted enclosures, the power indicator light shall be mounted on the side of the enclosure most visible from the major roadway.

- Electric Utility Meter Housing and Riser.  The electric meter housing and meter socket shall be supplied and installed by the Contractor. The Contractor is to coordinate the work to be performed and the materials required with the utility company to make the final connection at the power source.  Electric utility required risers, weather/service head, and any other materials necessary for connection shall also be included in the pay item.  Materials shall be in accordance with the electric utility’s requirements.  For ground-mounted service, the electric utility meter housing shall be mounted to the enclosure. The meter shall be supplied by the utility company.

- Surge Protector.  Overvoltage protection, with LED indicator, shall be provided for the 120 V load circuit by the means MOV and thermal fusing technology.  The response time shall be < 5 ns and operate within a range of –40°C to +85°C.  The surge protector shall be UL 1449 Listed.

- Circuit Breakers.  Circuit breakers shall be standard UL listed molded case, thermal-magnetic bolt-on type circuit breakers with trip free indicating handles.  120 V circuit breakers shall have an interrupting rating of not less than 65,000 rms symmetrical amperes.  Unless otherwise indicated, the main disconnect circuit breaker for the traffic signal controller shall be rated 60 A, 120 V and the auxiliary circuit breakers shall be rated 10 A, 120 V.

- Fuses and Fuseholders.  Fuses shall be small-dimensional cylindrical fuses of the dual element time-delay type.  The fuses shall be rated for 600 VAC and shall have a UL listed interrupting rating of not less than 10,000 rms symmetrical amperes at rated voltage.

- Ground and Neutral Bus Bars.  A single copper ground and neutral bus bar, mounted on the equipment panel shall be provided.  Ground and neutral conductors shall be separated on the bus bar.  Compression lugs, plus 2 spare lugs, shall be sized to accommodate the cables with the heads of the connector screws painted green for ground connections and white for neutral connections.

- Utility Services Connection.  The Contractor shall notify the utility company marketing representative a minimum of thirty (30) working days prior to the anticipated date of hook-up.  This 30-day advance notification will begin only after the utility company marketing representative has received service charge payments from the Contractor.  Prior to contacting the utility company marketing representative for service connection, the service installation controller cabinet and cable must be installed for inspection by the utility company.

- Ground Rod.  Ground rods shall be copper-clad steel, a minimum of 10 ft (3.0m) in length, and 3/4 in. (20mm) in diameter.  Ground rod resistance measurements to ground shall be 25 ohms or less.  If necessary additional rods shall be installed to meet resistance requirements at no additional cost to the Contract.

Installation.

- General.  The Contractor shall confirm the orientation of the traffic service installation and its door side with the Engineer prior to installation.  All conduit entrances into the service installation shall be sealed with a pliable waterproof material.

- Pole Mounted.  Brackets designed for pole mounting shall be used.  All mounting hardware shall be stainless steel.  Mounting height shall be as noted on the plans or as directed by the Engineer.

- Ground Mounted.  The service installation shall be mounted plumb and level on the foundation and fastened to the anchor bolts with hot-dipped galvanized or stainless steel nuts and washers.  The space between the bottom of the enclosure and the top of the foundation shall be caulked at the base with silicone.

Basis of Payment.

The service installation shall be paid for at the Contract unit price each for SERVICE INSTALLATION of the type specified which shall be payment in full for furnishing and installing the service installation complete.  The CONCRETE FOUNDATION, TYPE A, which includes the ground rod, shall be paid for separately.  SERVICE INSTALLATION, POLE MOUNTED shall include the 3/4 in. (20mm) grounding conduit, ground rod, and pole mount assembly.  Any charges by the utility companies shall be approved by the Engineer and paid for as an addition to the Contract according to Article 109.05 of the Standard Specifications.