# FIBER OPTIC TRACER CABLE

Effective: May 22, 2002

Revised: November 1, 2023

817.02TS

The cable shall meet the requirements of Section 817 of the Standard Specifications, except for the following:

Add the following to Article 817.03 of the Standard Specifications:

“In order to trace the fiber optic cable after installation, the tracer cable shall be installed in the same conduit as the fiber optic cable in locations shown on the plans.  The tracer cable shall be continuous, extended into the controller cabinet and terminated on a barrier type terminal strip mounted on the side wall of the controller cabinet.  The barrier type terminal strip and tracer cable shall be clearly marked and identified.  All tracer cable splices shall be kept to a minimum and shall incorporate maximum lengths of cable supplied by the manufacturer.  The tracer cable will be allowed to be spliced at handholes only.  The tracer cable splice shall use a Western Union Splice soldered with resin core flux and shall be soldered using a soldering iron.  Blow torches or other devices which oxidize copper cable shall not be allowed for soldering operations.  All exposed surfaces of the solder shall be smooth.  The splice shall be covered with a black shrink tube meeting UL 224 guidelines, Type V and rated 600V, minimum length 4 in. (100 mm) and with a minimum 1 in. (25 mm) coverage over the XLP insulation, underwater grade.”

Revise Article 817.05 of the Standard Specifications to read:

“Basis of Payment. The tracer cable shall be paid for separately as ELECTRIC CABLE IN CONDUIT, TRACER, NO. 14 1C per foot (meter), which price shall include all associated labor and material for installation.”