## NETWORK SWITCH

Effective: November 1, 2023

Revised: April 1, 2026

892.04TS

Description.

This item must consist of furnishing and installation of various network switches as shown in the plan. The network switches consist of Access, Distribution and Core Switch.

Materials. Materials must be according to the following:

  - General Requirements:

    - Management and Support Capabilities. Must include the following:

      - support full-duplex Ethernet

      - be capable Layer 2 LAN Base services

      - have American Standard Code for Information Interchange (ASCII) based configuration files for offline editing and bulk configuration

      - be managed using Simple Network Management Protocol (SNMP) Version 3.

      - be able to use Secure File Transfer Protocol (SFTP) to transfer configuration file to and from a central server.

      - be compliant with IEEE 802.1 and 802.3. Specifically, the switch must comply with the following IEEE 802.1 standards: (a) IEEE 802.1D - Media Access Control (MAC) Bridges, including Rapid Spanning Tree Protocol (RSTP). (b) IEEE 802.1Q - Virtual Local Area Network (VLAN) tagging and Multiple Spanning Tree Protocol (MSTP). (c) IEEE 802.1X (Port Based Network Access Protocol).

      - perform multicast filtering using Internet Group Management Protocol (IGMP) snooping.

      - support Address Resolution Protocol (ARP)

      - Need to have TACACS/RADIUS access via SSH

      - Need to support CDP protocol for neighbor reporting/discovery

      - Support for MAB security (ISE)

    - Power Requirements:

      - Input Voltage to Power Supply Modules: 100 to 240 VAC

      - Capable of using Redundant Power Supplies

      - Must use Manufacturer approved power supply.

    - Must utilize Single Mode Fiber Small Form-Factor Plug (SFP) Modules that have the following:

- Minimum performance of 1Gbps

- From the manufacturer of the switch.

- See plans for distance, type and quantity requirements

    - All ports must have Diagnostic light-emitting diodes (LED). These indicators must include link, activity, and power LEDs.

    - Must include a 1-year hardware support agreement and license (contract type SNT)

  - Additional Requirements for Distribution and Core Switches:

    - Switches must support the following Layer 3 capabilities:

      - Support of Enhanced Interior Gateway Routing Protocol (EIGRP).

      - Support of Border Gateway Protocol (BGP).

      - Internet Protocol Version 4 (IPv4);

      - Internet Protocol Version 6 (IPv6);

      - Open Shortest Path First (OSPF);

      - Generic Routing Encapsulation (GRE);

      - Inter-VLAN Internet Protocol (IP) routing for full Layer 3 routing between two or more VLANs;

      - Virtual Router Redundancy Protocol (VRRP);

      - IP multicast routing utilizing Protocol Independent Multicast (PIM) and Internet Group Management Protocol, Version 2 (IGMPv2).

      - Support for PIM sparse mode (PIM-SM) and PIM dense mode (PIM-DM);

      - Security utilizing Access Control Lists (ACLs).

  - Switch Types:

    - Access Switch:

- Must include:

        - General Requirements.

        - the following port types or better:

            - 10/100/1000 Mbps copper Ethernet ports, RJ-45 connector

            - FE/GE SFP ports

- Environmental Requirements:

        - Operating Temperature: -34° to +70°C

        - Humidity: 0 to 95% (non-condensing)

        - IEC/EN/EN61000-4-2 (Electro Static Discharge), 8kV air/6kV contact

        - IEC/EN 61000-4-3 (Radiated Immunity, 10 V/m 80-2000MHz, 3V/m 2000-2700MHz)

        - IEC/EN 61000-4-4 (Fast Transients - 2kV DC power, 2kV data line, 4kv earth)

        - IEC/EN 61000-4-5 (Surge 2 kV/1 kV DC power, 2 kV shielded and unshielded data line)

        - IEC/EN 61000-4-6 (Conducted Immunity, 10 V/emf 0.15-80MHz)

        - IEC/EN 61000-4-8 (Power Frequency Magnetic Field Immunity 30A/m 60 sec, 300A/m 3 sec)

        - IEC/EN 61000-4-9 (Pulse Magnetic Field Immunity 300A/m)

        - IEC/EN 61000-4-29 (Voltage Dips Immunity)

        - IEC 60068-2-27 (Operational Shock: 30G 11ms, half sine)

        - IEC 60068-2-27 (Non-Operational Shock 65-80G, trapezoidal)

        - IEC 60068-2-6, IEC 60068-2-64 (Operational Vibration)

        - EC 60068-2-6, IEC 60068-2-64, IEC 60068-2-47 (Non-operational Vibration)

    - Distribution Switch:

      - Must include:

          - General Requirements.

          - Additional Requirements for Distribution and Core Switches

          - The following port types or better:

            - 10/100/1000 Mbps copper Ethernet ports, RJ-45 connector

            - FE/GE SFP ports

      - Environmental Requirements:

          - Operating Temperature: -40° to +75°C

          - Operate in a cabinet enclosure

          - Humidity: 5 to 95% (non-condensing)

          - CISPR 24 / CISPR 35

          - EN55024 / EN55035

          - KN 35

          - EN 61000-4-2 Electro Static Discharge (air – 15kV, contact – 8kV)

          - EN 61000-4-3 Radiated RF (10V/m UTP, 20V/m STP)

          - EN 61000-4-4 Electromagnetic Fast Transients (4kV)

          - EN 61000-4-5 Surge (2KV/1KV Power, 4KV STP)

          - EN 61000-4-6 Conducted RF (10Vrms UTP)

          - EN 61000-4-8 Power Frequency Magnetic Field (1000A/m)

          - EN 61000-4-10 Damped Oscillatory Magnetic Field (100 A/m)

          - EN 61000-4-16 Conducted CM Disturbances (30V, Cont/ 300V, 1 sec)

          - EN 61000-4-17 Ripple Immunity DC Power (10%)

          - EN 61000-4-18 Damped Oscillatory Wave (2.5kV, 1MHz)

          - EN-61000-4-29 DC Voltage Dips and Interruptions

          - ANSI/ISA 12.12.01 (Class1, Div2 A-D)

          - EN 60079-0, -15 ATEX certificate (Class 1, Zone2 A-D)

          - EC 60079-0, 15 (report only)

          - UL 60079-0, 15

          - IEC 60068-2-27 (operational shock, 50G, 3ms, half sine)

          - IEC 60068-2-27 (non-operational shock, 65-80G, 9ms, trapezoidal)

          - IEC 60068-2-6 (vibration-sinusiodal, 5Hz-150Hz)

    - Core Switch:

      - Must include:

        - General Requirements.

        - Additional Requirements for Distribution and Core Switches

        - Network Port Requirements:

            - 48x 1/10/25G Gigabit Ethernet SFP ports

            - 4x 40/100G Uplink

            - Or better

      - Environmental requirements:

        - Operating Temperature: -5°C to +35°C (23° to 95° F)

        - Relative humidity operating: 10 to 85% (noncondensing)

        - Must be installed in a temperature-controlled environment.

Configuration.

Thirty (30) days prior to the installation of the network switches, The Contractor must deliver the switches, for configuration, to the Traffic Systems Center (TSC) located at 445 Harrison St Oak Park, IL.

The switches must be delivered with markings on the box indicating the cabinet the item will be installed in per the plans.  TSC will provide final network label on the switch.

After the switch is configured, the Contractor must coordinate an appointment to pick up the switches from the TSC and install it.

Installation.

Access and Distribution Switches are to be installed in cabinets identified in the plans.  Core Switches are only to be installed in temperature-controlled environments identified in the plans.

Documentation.

In addition to the initial submittal(s) prior to procurement, the Contractor must provide installation and operation manuals, documentation of exact equipment model and serial numbers, software/firmware version numbers, location installed in PDF formats on flash drive or via electronic delivery.

Basis of Payment.

This work will be paid for at the contract price per each for NETWORK SWITCH, (of the type specified), the price of which shall include all equipment, materials, and labor required to furnish, and install the switch, including all necessary connectors, cables, fiber optic jumpers, hardware, software and other peripheral equipment required to place the switch in operation to the satisfaction of the Engineer.